## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Network Waitaki Ltd
| Disclosure Date | 2025-08-31
| Disclosure Year (year ended) | 2025-03-31
Template for Schedule 10a
Prepared 16 February 2024.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Targeted Review 2024) Amendment Determination 2024 [2024] NZCC 2.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Network Waitaki Ltd
[15 empty] | For Year Ended | 2025-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | MF552 | Lake Waitaki GXP | N/A | 464FED | 2024-04-03 | 45385.3333 | 2024-04-03 16:39 | 45385.6937 | 0.92233 | 0.0017771 | 24 | 12456 | Planned | 11.0 Planned Shutdown | To Isolate 33kV Line (Being Constructed) & 11kV Line @ Lake Waitaki GXP to install New Pole 1 & Pole B and install new 33kV Line between Pole 41753 and new Pole B
10 |  | PR119 | Lake Ohau Rd | N/A | 490FED | 2024-04-03 | 45385.3375 | 2024-04-04 15:34 | 45386.6486 | 0.33173 | 0.00074047 | 10 | 4480 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms
11 |  | MF553 | Waitaki GXP | N/A | 464FED | 2024-04-04 | 45386.3479 | 2024-04-04 16:49 | 45386.7007 | 0.90278 | 0.0017771 | 24 | 12192 | Planned | 11.0 Planned Shutdown | To Isolate 11kV & 33kV Lines to reconfigure 33kV Network
12 |  | PR127 | Lake Ohau Rd | N/A | 490FED | 2024-04-04 | 45386.3771 | 2024-04-04 16:07 | 45386.6715 | 0.094187 | 0.00022214 | 3 | 1272 | Planned | 11.0 Planned Shutdown | Replacing Pole 17712 & 38863
13 |  | NJ429 | Kurow Duntroon Rd | N/A | 470FED | 2024-04-05 | 45387.3549 | 2024-04-05 14:22 | 45387.5986 | 1.0401 | 0.0030359 | 41 | 14046 | Planned | 11.0 Planned Shutdown | Replacing Pole 17177 and 11kVLinks Pole 17182
14 |  | F5051 | 344 Grants Rd | N/A | 411FED | 2024-04-07 | 45389.3632 | 2024-04-07 10:30 | 45389.4375 | 0.007923 | 7.4047e-05 | 1 | 107 | Unplanned | 6.0 Wildlife | Rat @ Pole 32772 blew 11kV Links Pole 32770
15 |  | F4649 F16210 | Crm Spring Field @ Fortification Rd | N/A | 416FED | 2024-04-08 | 45390.5208 | 2024-04-08 13:35 | 45390.566 | 0.26953 | 0.0041466 | 56 | 3640 | Unplanned | 8.0 Defective Equipment | Broken Kidney on Pole 30377
16 |  | F16180 | Otematata Substation | N/A | 425FED | 2024-04-09 | 45391.3354 | 2024-04-09 08:27 | 45391.3521 | 0.22747 | 0.009478 | 128 | 3072 | Planned | 11.0 Planned Shutdown | Planned Outage for Close Approach Permit 8593
17 |  | NJ432 NJ433 16179 | Livingston Rd / Danseys Pass Rd / Dip Hill Rd | N/A | 421FED | 2024-04-09 | 45391.3486 | 2024-04-09 16:45 | 45391.6979 | 1.7542 | 0.0058497 | 79 | 23691 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms and Maintenance & Faulted ABS1143
18 |  | F4436 | 234 Papakaio Rd | N/A | 457FED | 2024-04-10 | 45392.241 | 2024-04-10 06:30 | 45392.2708 | 0.003184 | 7.4047e-05 | 1 | 43 | Unplanned | 6.0 Wildlife | Rat Blew 11kV Links Pole 42086 (Pole 23006)
19 |  | F5053 | 331 Gards Rd | N/A | 411FED | 2024-04-10 | 45392.3486 | 2024-04-10 11:00 | 45392.4583 | 0.011699 | 7.4047e-05 | 1 | 158 | Unplanned | 9.0 Cause Unknown | No Power 11kV Links Blown @ Pole 32762
20 |  | PR131 | Homestead | N/A | 430FED | 2024-04-10 | 45392.3653 | 2024-04-10 17:06 | 45392.7125 | 1.6231 | 0.0033321 | 45 | 21920 | Planned | 11.0 Planned Shutdown | Replacing Pole 15772 and H Structure Pole 15768/15769
21 |  | F16181 | Rocklands Rd | N/A | 416FED | 2024-04-16 | 45398.3688 | 2024-04-16 08:54 | 45398.3708 | 0.037097 | 0.012366 | 167 | 501 | Unplanned | 5.0 Third party Interference | NWL Contractor was Tree Felling Rocklands Rd and a Branch hit the 11kV Line
22 |  | PR145 | Oamaru Duntroon Rd | N/A | 470FED | 2024-04-16 | 45398.3785 | 2024-04-16 11:56 | 45398.4972 | 0.15194 | 0.00088856 | 12 | 2052 | Planned | 11.0 Planned Shutdown | Replacing Transformer T4505
23 |  | NJ435 | Georgetown Pukeuri Rd | N/A | 456FED | 2024-04-17 | 45399.366 | 2024-04-17 15:22 | 45399.6403 | 0.29248 | 0.00074047 | 10 | 3950 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarm and Installing Transformer
24 |  | NJ437A | 11kV Line Katiki | N/A | 480FED | 2024-04-18 | 45400.3347 | 2024-04-18 16:16 | 45400.6778 | 0.62184 | 0.0012588 | 17 | 8398 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & Conductor
25 |  | NJ437B | 11kV Line Katiki | N/A | 480FED | 2024-04-19 | 45401.3361 | 2024-04-19 15:15 | 45401.6354 | 0.54254 | 0.0012588 | 17 | 7327 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & Conductor
26 |  | NJ437C | 11kV Line Katiki | N/A | 480FED | 2024-04-23 | 45405.3382 | 2024-04-23 16:29 | 45405.6868 | 0.63191 | 0.0012588 | 17 | 8534 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & Conductor
27 |  | NJ438A | 11kV Line Katiki Straight | N/A | 480FED | 2024-04-24 | 45406.3333 | 2024-04-24 15:58 | 45406.6653 | 1.0972 | 0.0022954 | 31 | 14818 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & 11kV Conductor
28 |  | NJ438B | 11kV Line Katiki Straight | N/A | 480FED | 2024-04-26 | 45408.334 | 2024-04-26 14:43 | 45408.6132 | 0.92277 | 0.0022954 | 31 | 12462 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & 11kV Conductor
29 |  | F5206 | 68/69 Grants Rd | N/A | 483FED | 2024-04-29 | 45411.3278 | 2024-04-29 09:45 | 45411.4062 | 0.016735 | 0.00014809 | 2 | 226 | Unplanned | 6.0 Wildlife | Swan Hit 11kV Line between Pole 25787 17285 Blew 11kV Links Pole 17284
30 |  | NJ438C | 11kV Line Katiki Straight | N/A | 480FED | 2024-04-29 | 45411.3333 | 2024-04-29 16:23 | 45411.6826 | 1.1546 | 0.0022954 | 31 | 15593 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & 11kV Conductor
31 |  | NJ439 | Brinkburn St Oamaru | N/A | 409FED | 2024-04-29 | 45411.3826 | 2024-04-29 16:55 | 45411.7049 | 1.4774 | 0.003184 | 43 | 19952 | Planned | 11.0 Planned Shutdown | Replacing Pole 37589 & Pole 11994
32 |  | F5059 | Omarama Twizel 33kV Line | N/A | 2192FED | 2024-04-30 | 45412.0674 | 2024-04-30 03:55 | 45412.1632 | 0.80444 | 0.049389 | 667 | 10864 | Unplanned | 9.0 Cause Unknown | CB2192 Tripped
33 |  | NJ438D | 11kV Line Katiki Straight | N/A | 480FED | 2024-04-30 | 45412.3333 | 2024-04-30 16:07 | 45412.6715 | 1.1179 | 0.0022954 | 31 | 15097 | Planned | 11.0 Planned Shutdown | Replacing, Poles Crossarms & 11kV Conductor
34 |  | F4668 | 11kV Line Peaks Rd | N/A | 449FED | 2024-04-30 | 45412.5722 | 2024-04-30 14:22 | 45412.5986 | 0.04502 | 0.0011847 | 16 | 608 | Unplanned | 8.0 Defective Equipment | No Nuts on Insulaotrs, Replaced Crossarms Pole 38095
35 |  | F5160 | 741 Weston Ngapara Rd | N/A | 449FED | 2024-04-30 | 45412.8146 | 2024-05-01 07:50 | 45413.3264 | 0.054572 | 7.4047e-05 | 1 | 737 | Unplanned | 9.0 Cause Unknown | Blown 11kV Links Pole 41699
36 |  | F4712 WA32086 | R686/741 Weston Ngapara Rd | N/A | 449FED | 2024-05-01 | 45413.2917 | 2024-05-01 07:53 | 45413.3285 | 0.0039245 | 7.4047e-05 | 1 | 53 | Unplanned | 9.0 Cause Unknown | 11kV Link Blown at Pole 41699
37 |  | NJ443 | McIntyre 11kv Line Ruataniwha Substation | N/A | 526FED | 2024-05-02 | 45414.3958 | 2024-05-02 13:25 | 45414.559 | 0.31322 | 0.0013328 | 18 | 4230 | Planned | 11.0 Planned Shutdown | Connecting New Network 11kV Bypass Line
38 |  | F4446 | 22 Kuriheka Rd | N/A | 415FED | 2024-05-03 | 45415.3465 | 2024-05-03 09:45 | 45415.4062 | 0.012736 | 0.00014809 | 2 | 172 | Unplanned | 9.0 Cause Unknown | 11kV Links Blown @ Pole 26571
39 |  | NJ440 | 11kV Line Teschemakers Rd | N/A | 414FED | 2024-05-03 | 45415.3542 | 2024-05-03 15:05 | 45415.6285 | 0.20474 | 0.00051833 | 7 | 2765 | Planned | 11.0 Planned Shutdown | Replacing 11kV Pole 38225 & 25063 and Replacing 11kV Links Pole 25057 & 25070
40 |  | NJ448 | 11kV Line Taipo Rd | N/A | 414FED | 2024-05-03 | 45415.3576 | 2024-05-03 16:46 | 45415.6986 | 0.21814 | 0.00044428 | 6 | 2946 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms
41 |  | F4681 | Frenchs Rd | N/A | 415FED | 2024-05-10 | 45422.5007 | 2024-05-10 12:26 | 45422.5181 | 0.038874 | 0.001555 | 21 | 525 | Unplanned | 8.0 Defective Equipment | No Nuts on 11kV Insulator at Pole 25709
42 |  | F5060 F16087 | Ngapara Zone Substation | N/A | 501FED | 2024-05-11 | 45423.7493 | 2024-05-11 19:13 | 45423.8007 | 0.61088 | 0.039763 | 537 | 8250 | Unplanned | 8.0 Defective Equipment | VT on T1 transformer Faulted
43 |  | PR157A | Pinot Noir Court Omarama | N/A | 423FED | 2024-05-15 | 45427.3889 | 2024-05-15 16:01 | 45427.6674 | 0.35631 | 0.00088856 | 12 | 4812 | Planned | 11.0 Planned Shutdown | Replacing Transformer T5510.1 and installing new SFB
44 |  | PR157B/WA32896 | Pinot Noir Court Omarama | N/A | 423FED | 2024-05-16 | 45428.4049 | 2024-05-16 15:15 | 45428.6354 | 0.27901 | 0.0017771 | 24 | 3768 | Unplanned | 8.0 Defective Equipment | Replacing Transformer T5510.1
45 |  | F5104 | 344 Grants Rd | N/A | 411FED | 2024-05-17 | 45429.3306 | 2024-05-17 22:03 | 45429.9187 | 0.0094039 | 7.4047e-05 | 1 | 127 | Unplanned | 6.0 Wildlife | Rodents Blew 11kV Links Pole 32770
46 |  | F5103 | 1119 Georgetown Pukeuri Rd | N/A | 456FED | 2024-05-18 | 45430.1701 | 2024-05-18 05:07 | 45430.2132 | 0.0091818 | 0.00014809 | 2 | 124 | Unplanned | 6.0 Wildlife | Possom Blew 11kV Links @ Pole 23878
47 |  | F5105 | 115 Maheno Kakanui Rd | N/A | 416FED | 2024-05-18 | 45430.3285 | 2024-05-18 09:08 | 45430.3806 | 0.0055535 | 7.4047e-05 | 1 | 75 | Unplanned | 6.0 Wildlife | Possom Blew 11KV Links @ Pole 71933
48 |  | PR164 | Richmond Rd | N/A | 435FED | 2024-05-20 | 45432.4083 | 2024-05-20 12:07 | 45432.5049 | 0.051462 | 0.00037023 | 5 | 695 | Planned | 11.0 Planned Shutdown | Change Cross arms on Pole 41807 and Resag 11kV Line between Pole 22227 and 33042
49 |  | PR162 | Richmond Rd | N/A | 435FED | 2024-05-20 | 45432.4111 | 2024-05-20 15:56 | 45432.6639 | 0.080859 | 0.00022214 | 3 | 1092 | Planned | 11.0 Planned Shutdown | Changing Pole 21930 live line
50 |  | NJ455 | 33kV/11kV Line Twizel Omarama | N/A | 492FED | 2024-05-21 | 45433.3375 | 2024-05-21 17:43 | 45433.7382 | 0.42096 | 0.00074047 | 10 | 5685 | Planned | 11.0 Planned Shutdown | Installing Temp Links Pole 39776, Replacing Poles, Replace ABS3411
51 |  | NJ449 | 11kV Line Papakaio Rd | N/A | 457FED | 2024-05-21 | 45433.3778 | 2024-05-21 15:25 | 45433.6424 | 1.0438 | 0.0027397 | 37 | 14097 | Planned | 11.0 Planned Shutdown | Isolating 11kV Line @ Pole 42088 for Omexon to change Transpower Pole
52 |  | PI151 | 11kV Line Mckenzie Rd | N/A | 421FED | 2024-05-21 | 45433.4049 | 2024-05-21 16:43 | 45433.6965 | 0.1866 | 0.00044428 | 6 | 2520 | Planned | 11.0 Planned Shutdown | Replacing LV Pole 37163c and 11kV Crossarm on Pole 22465
53 |  | NJ456 | Twizel Omarama Rd | N/A | 492FED | 2024-05-22 | 45434.3535 | 2024-05-22 15:49 | 45434.659 | 0.29174 | 0.00066642 | 9 | 3940 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles
54 |  | NJ450 | 11kV Line Georgetown Pukeuri Rd | N/A | 456FED | 2024-05-22 | 45434.3618 | 2024-05-22 15:19 | 45434.6382 | 0.32418 | 0.00081451 | 11 | 4378 | Planned | 11.0 Planned Shutdown | Isolating 11kV Line @ Pole 23796 for Omexon to change Transpower Pole
55 |  | PI157 | Twizel Omarama Rd | N/A | 492FED | 2024-05-23 | 45435.3389 | 2024-05-23 13:52 | 45435.5778 | 0.22303 | 0.00066642 | 9 | 3012 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles
56 |  | F15988 | Serpentine Rd | N/A | 415FED | 2024-05-26 | 45438.1937 | 2024-05-26 09:25 | 45438.3924 | 0.68871 | 0.010663 | 144 | 9301 | Unplanned | 2.0 Vegetation | Tree Through 11kV Line Sepentine Rd Burnt Off 11kV Jumper Pole 18598
57 |  | F5169 | Danseys Pass | N/A | 421FED | 2024-05-26 | 45438.5868 | 2024-05-26 20:53 | 45438.8701 | 0.29337 | 0.0072566 | 98 | 3962 | Unplanned | 3.0 Adverse Weather | Wire off insulator @ Pole 23357
58 |  | F5067 | Smith Rd | N/A | 421FED | 2024-05-26 | 45438.6549 | 2024-05-26 19:31 | 45438.8132 | 0.36187 | 0.0034802 | 47 | 4887 | Unplanned | 2.0 Vegetation | Trees Brought down 11kV Line Smith Rd near Pole 22748
59 |  | NJ459A | 11kV Line Whartons Rd | N/A | 415FED | 2024-05-27 | 45439.359 | 2024-05-27 15:35 | 45439.6493 | 0.52618 | 0.0012588 | 17 | 7106 | Planned | 11.0 Planned Shutdown | Replacing Crossarms, Pole 25543 and 11kV Conductor between Pole 37922 - 25554
60 |  | NJ458A | Twizel Omarama Rd | N/A | 492FED | 2024-05-27 | 45439.4222 | 2024-05-27 16:11 | 45439.6743 | 0.026879 | 7.4047e-05 | 1 | 363 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles
61 |  | PR178 | Tokarahi Tapui Rd | N/A | 421FED | 2024-05-27 | 45439.4583 | 2024-05-27 12:51 | 45439.5354 | 0.016438 | 0.00014809 | 2 | 222 | Planned | 11.0 Planned Shutdown | Hedge Trimming @ Pole 10098
62 |  | NJ458B | Twizel Omarama Rd | N/A | 492FED | 2024-05-28 | 45440.3333 | 2024-05-28 16:40 | 45440.6944 | 0.038504 | 7.4047e-05 | 1 | 520 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles
63 |  | NJ459B | 11kV Line Whartons Rd | N/A | 415FED | 2024-05-28 | 45440.3562 | 2024-05-28 17:08 | 45440.7139 | 0.64828 | 0.0012588 | 17 | 8755 | Planned | 11.0 Planned Shutdown | Replacing Crossarms, Pole 25543 and 11kV Conductor between Pole 37922 - 25554
64 |  | NJ458C | Twizel Omarama Rd | N/A | 492FED | 2024-05-29 | 45441.3271 | 2024-05-29 15:36 | 45441.65 | 0.034432 | 7.4047e-05 | 1 | 465 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles
65 |  | F5172 WA27427 | 8 industrial Place | N/A | 438FED | 2024-05-29 | 45441.409 | 2024-05-29 10:37 | 45441.4424 | 0.0035542 | 7.4047e-05 | 1 | 48 | Unplanned | 8.0 Defective Equipment | Replacing LV Pole Fuse Base @ Pole 28008
66 |  | F5173 | Double Hill Rd | N/A | 417FED | 2024-05-29 | 45441.4639 | 2024-05-29 11:54 | 45441.4958 | 0.04428 | 0.00096261 | 13 | 598 | Unplanned | 8.0 Defective Equipment | 11kV Wire Floating @ Pole 27319
67 |  | F5175A | 75 Awakino Rd | N/A | 411FED | 2024-05-29 | 45441.4917 | 2024-05-29 12:04 | 45441.5028 | 0.066346 | 0.0041466 | 56 | 896 | Unplanned | 2.0 Vegetation | Tree Through 11kV Line between Pole 75662 - Pole 71165
68 |  | F5174 | Double Hill Rd | N/A | 417FED | 2024-05-29 | 45441.6056 | 2024-05-29 15:26 | 45441.6431 | 0.051981 | 0.00096261 | 13 | 702 | Unplanned | 8.0 Defective Equipment | 11kV Wire Floating @ Pole 27319
69 |  | NJ465 | Twizel Omarama Rd | N/A | 492FED | 2024-05-30 | 45442.3313 | 2024-05-30 15:23 | 45442.641 | 0.033025 | 7.4047e-05 | 1 | 446 | Planned | 11.0 Planned Shutdown | Replacing 33kV/11kV poles
70 |  | PR168 | Pukeuri-Oamaru Rd | N/A | 432FED | 2024-05-30 | 45442.3542 | 2024-05-30 14:58 | 45442.6236 | 0.02873 | 7.4047e-05 | 1 | 388 | Planned | 11.0 Planned Shutdown | Replacing Transformer @ Pole 25210
71 |  | F5214 | 6 Easons Rd | N/A | 479FED | 2024-05-30 | 45442.5347 | 2024-05-30 13:33 | 45442.5646 | 0.060496 | 0.0014069 | 19 | 817 | Unplanned | 8.0 Defective Equipment | Floating 11kV Wire @ Pole 11787
72 |  | F5117 | Haven St Moerkai | N/A | 480FED | 2024-05-31 | 45443.0236 | 2024-05-31 02:45 | 45443.1146 | 0.048501 | 0.00037023 | 5 | 655 | Unplanned | 9.0 Cause Unknown | Blown 11kV Link Pole 40094
73 |  | PR179 | Gardiners Rd | N/A | 416FED | 2024-05-31 | 45443.4028 | 2024-05-31 10:18 | 45443.4292 | 0.0056275 | 0.00014809 | 2 | 76 | Planned | 11.0 Planned Shutdown | Remove LV service from Pole 36741
74 |  | NJ457 | Georgetown Pukeuri Rd | N/A | 456FED | 2024-05-31 | 45443.4243 | 2024-05-31 11:31 | 45443.4799 | 0.011847 | 0.00014809 | 2 | 160 | Planned | 11.0 Planned Shutdown | Resag LV conductor between Pole 23821 - Pole 36745
75 |  | F5069 | 407 Lake Ohau Rd | N/A | 490FED | 2024-05-31 | 45443.7139 | 2024-05-31 19:14 | 45443.8014 | 0.01866 | 0.00014809 | 2 | 252 | Unplanned | 9.0 Cause Unknown | Blown 11kV Link Pole 35769
76 |  | F5180 | 67 Dunrobin Rd | N/A | 486FED | 2024-05-31 | 45443.875 | 2024-05-31 21:41 | 45443.9035 | 0.0060718 | 0.00014809 | 2 | 82 | Unplanned | 6.0 Wildlife | Rodents Blew 11kV Links @ Pole 16408
77 |  | F16094A | 11kV Line Ruatihwa | N/A | 526FED | 2024-06-01 | 45444.1701 | 2024-06-01 07:23 | 45444.3076 | 0.57194 | 0.0029619 | 40 | 7724 | Unplanned | 8.0 Defective Equipment | Broken Strand on 11kV Jumper at Pole 72036
78 |  | F5119 F16095 | 11kV Line 47 Dip Hill Rd | N/A | 421FED | 2024-06-01 | 45444.4604 | 2024-06-01 14:45 | 45444.6146 | 0.9863 | 0.0044428 | 60 | 13320 | Unplanned | 8.0 Defective Equipment | Broken 11kV Pole 22618
79 |  | F5070 F16096 | Serpentine Rd | N/A | 415FED | 2024-06-01 | 45444.7021 | 2024-06-01 20:18 | 45444.8458 | 0.21163 | 0.0045909 | 62 | 2858 | Unplanned | 2.0 Vegetation | Tree down on 11kV between Pole 11266 and Pole 11267
80 |  | F5181 F16097 | 11kV Line 117 Grants Rd | N/A | 473FED | 2024-06-01 | 45444.7278 | 2024-06-01 19:56 | 45444.8306 | 0.16231 | 0.0030359 | 41 | 2192 | Unplanned | 8.0 Defective Equipment | Broken Binder caused 11kV Wire on ground Grants Rd
81 |  | F4715 | Weston Ngapara Rd | N/A | 449FED | 2024-06-01 | 45444.8792 | 2024-06-01 21:36 | 45444.9 | 0.0022214 | 7.4047e-05 | 1 | 30 | Unplanned | 6.0 Wildlife | Blown 11kV Link Pole 41699
82 |  | F5073 | 741 Weston Ngapara Rd | N/A | 449FED | 2024-06-03 | 45446.8049 | 2024-06-03 19:52 | 45446.8278 | 0.0024435 | 7.4047e-05 | 1 | 33 | Unplanned | 6.0 Wildlife | Rodent Blew 11kV Link at Pole 41699
83 |  | NJ466 | 11kV Line Twizel Omarama | N/A | 491FED | 2024-06-04 | 45447.4125 | 2024-06-04 16:18 | 45447.6792 | 0.19904 | 0.00051833 | 7 | 2688 | Planned | 11.0 Planned Shutdown | Replacing Poles 21156, 36255. and between Pole 21149 - 36256
84 |  | NJ462 WA36322 | 11kV Line Fortification Rd | N/A | 416FED | 2024-06-05 | 45448.3333 | 2024-06-05 17:05 | 45448.7118 | 3.0352 | 0.0057016 | 77 | 40990 | Planned | 11.0 Planned Shutdown | Replacing Crossarms, Poles, Stub Poles
85 |  | NJ467A | 33kV 11kV Lines Omarama Twizel | N/A | 491FED | 2024-06-05 | 45448.3333 | 2024-06-11 16:28 | 45454.6861 | 0.26331 | 0.00051833 | 7 | 3556 | Planned | 11.0 Planned Shutdown | Replacing Poles
86 |  | PR188 | 11kV Line Hectors Rd | N/A | 483FED | 2024-06-05 | 45448.3458 | 2024-06-05 14:11 | 45448.591 | 0.41822 | 0.0011847 | 16 | 5648 | Planned | 11.0 Planned Shutdown | Tree Felling between Pole 40317 and Pole 870169
87 |  | NJ467B | 33kV 11kV Lines Omarama Twizel | N/A | 491FED | 2024-06-06 | 45449.3347 | 2024-06-11 16:46 | 45454.6986 | 0.2716 | 0.00051833 | 7 | 3668 | Planned | 11.0 Planned Shutdown | Replacing Poles
88 |  | PR181 | 11kV Line Buzan Rd | N/A | 415FED | 2024-06-07 | 45450.3333 | 2024-06-07 13:15 | 45450.5521 | 0.069974 | 0.00022214 | 3 | 945 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms, Replacing Conductor between Pole 26550 - Pole 26502
89 |  | NJ467C | 33kV 11kV Lines Omarama Twizel | N/A | 491FED | 2024-06-07 | 45450.3382 | 2024-06-07 14:50 | 45450.6181 | 0.20889 | 0.00051833 | 7 | 2821 | Planned | 11.0 Planned Shutdown | Replacing Poles
90 |  | WA16773 | Livingston Duntroon Rd | N/A | 470FED | 2024-06-07 | 45450.5389 | 2024-06-07 14:13 | 45450.5924 | 0.079822 | 0.0010367 | 14 | 1078 | Unplanned | 4.0 Adverse Environment | Isolating 11kV Line for Boulder Removal from Cliff Livingstone Duntroon Rd
91 |  | NJ467D | 33kV 11kV Lines Omarama Twizel | N/A | 491FED | 2024-06-10 | 45453.4361 | 2024-06-10 16:41 | 45453.6951 | 0.19334 | 0.00051833 | 7 | 2611 | Planned | 11.0 Planned Shutdown | Replacing Poles
92 |  | NJ467E | 33kV 11kV Lines Omarama Twizel | N/A | 491FED | 2024-06-11 | 45454.334 | 2024-06-11 16:22 | 45454.6819 | 0.25968 | 0.00051833 | 7 | 3507 | Planned | 11.0 Planned Shutdown | Replacing Poles
93 |  | NJ470 | 11kV Line Pukeuri Hilderthorpe Rd | N/A | 478FED | 2024-06-11 | 45454.3583 | 2024-06-11 14:55 | 45454.6215 | 0.44902 | 0.0011847 | 16 | 6064 | Planned | 11.0 Planned Shutdown | Replacing 11kV Crossarms, LV Poles, LV Arms
94 |  | NJ471A | Pukeuri Hilderthorpe Rd | N/A | 478FED | 2024-06-12 | 45455.3333 | 2024-06-12 15:43 | 45455.6549 | 0.90966 | 0.0019993 | 27 | 12285 | Planned | 11.0 Planned Shutdown | Replacing Crossarms & Poles and Stub Pole
95 |  | NJ467F | 33kV 11kV Lines Omarama Twizel | N/A | 491FED | 2024-06-12 | 45455.334 | 2024-06-12 16:43 | 45455.6965 | 0.27057 | 0.00051833 | 7 | 3654 | Planned | 11.0 Planned Shutdown | Replacing Poles
96 |  | F16099 | Richmond Rd | N/A | 435FED | 2024-06-12 | 45455.5597 | 2024-06-12 15:18 | 45455.6375 | 0.02488 | 0.00022214 | 3 | 336 | Unplanned | 8.0 Defective Equipment | Isolation to Replace Crossarm on Pole 34305
97 |  | NJ467G | 33kV 11kV Lines Omarama Twizel | N/A | 491FED | 2024-06-13 | 45456.334 | 2024-06-13 22:40 | 45456.9444 | 0.082414 | 0.00051833 | 7 | 1113 | Planned | 11.0 Planned Shutdown | Replacing Poles
98 |  | NJ471B | Pukeuri Hilderthorpe Rd | N/A | 478FED | 2024-06-13 | 45456.3403 | 2024-06-13 13:08 | 45456.5472 | 0.57979 | 0.0019993 | 27 | 7830 | Planned | 11.0 Planned Shutdown | Replacing Crossarms & Poles and Stub Pole
99 |  | F16100 | Omarama Ave | N/A | 423FED | 2024-06-13 | 45456.5153 | 2024-06-13 14:13 | 45456.5924 | 1.0411 | 0.028952 | 391 | 14060 | Unplanned | 5.0 Third party Interference | Car vs Pole 14912 Omarama Ave, 11kV Wire hanging in LV
100 |  | PR196 | 11kV Line Livingstone Duntroon Rd | N/A | 470FED | 2024-06-17 | 45460.3868 | 2024-06-17 16:10 | 45460.6736 | 0.27523 | 0.00066642 | 9 | 3717 | Planned | 11.0 Planned Shutdown | Replacing Poles , Crossarms , Running 3 Phase Conductor between Pole #22655 - #73158 and installing new Transformer
101 |  | NJ481A | 11kV Line Omarama Twizel Rd | N/A | 491FED | 2024-06-18 | 45461.334 | 2024-06-18 16:19 | 45461.6799 | 0.55313 | 0.0011107 | 15 | 7470 | Planned | 11.0 Planned Shutdown | Replacing Poles and Installing Temp Links at Pole 21233a/b
102 |  | NJ479 | 11kV Line Glenavy Hilderthorpe Rd | N/A | 478FED | 2024-06-18 | 45461.3396 | 2024-06-18 15:11 | 45461.6326 | 0.59371 | 0.0014069 | 19 | 8018 | Planned | 11.0 Planned Shutdown | Replacing Crossarms, Poles and Install Transformer at Pole 24222
103 |  | NJ476 | 11kV Line Redcastle Rd | N/A | 436FED | 2024-06-18 | 45461.5938 | 2024-06-18 15:37 | 45461.6507 | 0.0060718 | 7.4047e-05 | 1 | 82 | Planned | 11.0 Planned Shutdown | Removing LV line between Pole 33277 - 30868, Install new LV cabe from Pole 30868 to Pole 33277 and install SFB
104 |  | NJ481B | 11kV Line Omarama Twizel Rd | N/A | 491FED | 2024-06-19 | 45462.3333 | 2024-06-19 13:46 | 45462.5736 | 0.3843 | 0.0011107 | 15 | 5190 | Planned | 11.0 Planned Shutdown | Replacing Poles and Installing Temp Links at Pole 21233a/b
105 |  | NJ480 | 11kV Line Glenavy Hilderthorpe Rd | N/A | 478FED | 2024-06-19 | 45462.3333 | 2024-06-19 14:45 | 45462.6146 | 0.76438 | 0.0019993 | 27 | 10323 | Planned | 11.0 Planned Shutdown | Replacing Crossarms & Poles
106 |  | NJ475 | Georgetown Pukeuri Rd | N/A | 456FED | 2024-06-20 | 45463.3833 | 2024-06-20 16:30 | 45463.6875 | 0.064865 | 0.00014809 | 2 | 876 | Planned | 11.0 Planned Shutdown | Replacing ABS1041 Peebles with New TSW1711 Peebles
107 |  | PR198 | 11kV Line Mcpherson Rd | N/A | 454FED | 2024-06-21 | 45464.3542 | 2024-06-21 13:43 | 45464.5715 | 0.78934 | 0.0029619 | 40 | 10660 | Planned | 11.0 Planned Shutdown | Replacing Pole 22345 and Removing LV span between Pole 22345 and 22344
108 |  | PR199 | 11kV Line Barrie Rd | N/A | 456FED | 2024-06-24 | 45467.3958 | 2024-06-24 12:53 | 45467.5368 | 0.075157 | 0.00037023 | 5 | 1015 | Planned | 11.0 Planned Shutdown | Replacing Pole 23554, Replacing Crossarm on Pole 23547 and fit stay insulator
109 |  | NJ468 NJ469 | 11kV Line Ferry Rd | N/A | 454FED | 2024-06-24 | 45467.4167 | 2024-06-24 15:44 | 45467.6556 | 0.23576 | 0.001555 | 21 | 3184 | Planned | 11.0 Planned Shutdown | To Replace 11kV Crossarms, 11kV Links & Transformer at Pole 22082
110 |  | F5219 | 11kV Line Light House Rd | N/A | 480FED | 2024-06-24 | 45467.4278 | 2024-06-24 16:24 | 45467.6833 | 0.094187 | 0.00059237 | 8 | 1272 | Unplanned | 8.0 Defective Equipment | 11kV Link Blown in 11kV Cubicle Light House Rd
111 |  | F16212 | 11kV Wansbeck St RMU | N/A | 409FED | 2024-06-24 | 45467.7694 | 2024-06-24 19:29 | 45467.8118 | 3.9019 | 0.08508 | 1149 | 52695 | Unplanned | 8.0 Defective Equipment | 11kV Wansbeck St RMU Faulted
112 |  | NJ483 | 11kV Line Glenavy Hilderthorpe Rd | N/A | 478FED | 2024-06-26 | 45469.3431 | 2024-06-26 15:05 | 45469.6285 | 1.7956 | 0.0043688 | 59 | 24249 | Planned | 11.0 Planned Shutdown | Replacing Crossarms & Poles
113 |  | PR201 | 11kV Line Hakataramea Rd | N/A | 413FED | 2024-06-27 | 45470.3938 | 2024-06-27 13:49 | 45470.5757 | 0.058201 | 0.00022214 | 3 | 786 | Planned | 11.0 Planned Shutdown | Relocating Service Fuse Box
114 |  | F15992 | R664 | N/A | 421FED | 2024-07-01 | 45474.0604 | 2024-07-01 03:20 | 45474.1389 | 0.25287 | 0.0034061 | 46 | 3415 | Unplanned | 9.0 Cause Unknown | R664 Tripped
115 |  | PR202 | 11kV Line Pringles Gully Rd | N/A | 421FED | 2024-07-01 | 45474.391 | 2024-07-01 10:55 | 45474.4549 | 0.027249 | 0.00029619 | 4 | 368 | Planned | 11.0 Planned Shutdown | New Tx and Tighten and double Nut H Structure Pole 817008
116 |  | NJ484 | LV Line Cosy Dell Rd | N/A | 479FED | 2024-07-01 | 45474.4083 | 2024-07-01 14:34 | 45474.6069 | 0.042355 | 0.00014809 | 2 | 572 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and LV Conductor
117 |  | F16215 | 826 Kanaui Valley Rd | N/A | 483FED | 2024-07-01 | 45474.6139 | 2024-07-01 15:51 | 45474.6604 | 0.12092 | 0.0051092 | 69 | 1633 | Unplanned | 5.0 Third party Interference | Truck Hit 11kV Line at Pole 71041
118 |  | NJ485 | 11kV Line Ferry Rd | N/A | 454FED | 2024-07-02 | 45475.3576 | 2024-07-02 16:22 | 45475.6819 | 1.314 | 0.0028138 | 38 | 17746 | Planned | 11.0 Planned Shutdown | Replacing Crossarms and Poles
119 |  | F16216 | Ruatanhiwa Substation | N/A | 526FED | 2024-07-02 | 45475.5625 | 2024-07-02 13:40 | 45475.5694 | 0.012588 | 0.0012588 | 17 | 170 | Unplanned | 8.0 Defective Equipment | Emergency shutdown to shift OPEN Point at Ruantaniwha Sub
120 |  | PR205 | 11kV Line Nicholson Rd | N/A | 480FED | 2024-07-03 | 45476.3542 | 2024-07-03 14:07 | 45476.5882 | 0.34935 | 0.0010367 | 14 | 4718 | Planned | 11.0 Planned Shutdown | Replace Crossarms and Tx on Pole 10446
121 |  | PR203 | 11kV Line Weston Ngapara Rd | N/A | 449FED | 2024-07-04 | 45477.3333 | 2024-07-04 16:41 | 45477.6951 | 2.5847 | 0.0049611 | 67 | 34907 | Planned | 11.0 Planned Shutdown | Replacing Crossarms and Poles
122 |  | PR206 | 11kV Line Awamoa | N/A | 416FED | 2024-07-05 | 45478.3333 | 2024-07-05 14:24 | 45478.6 | 0.39807 | 0.0010367 | 14 | 5376 | Planned | 11.0 Planned Shutdown | Replacing Crossarms, Poles and Reconductoring
123 |  | F5144 | 15 Cosy Dell Rd | N/A | 479FED | 2024-07-05 | 45478.5694 | 2024-07-05 15:18 | 45478.6375 | 0.014513 | 0.00014809 | 2 | 196 | Unplanned | 9.0 Cause Unknown | No Power, Links Blown
124 |  | F12624 | Te Akatarawa Rd | N/A | 464FED | 2024-07-06 | 45479.6632 | 2024-07-07 13:56 | 45480.5806 | 1.3434 | 0.0041466 | 56 | 18142 | Unplanned | 8.0 Defective Equipment | Insulator came out of xarm and conductor burnt through
125 |  | PR190 | 33/11kV Lines Whitstone Five Forks Rd | N/A | 533FED | 2024-07-08 | 45481.3562 | 2024-07-08 16:18 | 45481.6792 | 0.30989 | 0.00066642 | 9 | 4185 | Planned | 11.0 Planned Shutdown | Replace 33/11kV Pole 825924
126 |  | MF529 | 11kV Line Island Stream Rd | N/A | 415FED | 2024-07-08 | 45481.3951 | 2024-07-08 12:47 | 45481.5326 | 0.029322 | 0.00014809 | 2 | 396 | Planned | 11.0 Planned Shutdown | Trim Trees Between poles 25960 & 12602
127 |  | PR213 | 11kV Line Light House Rd | N/A | 480FED | 2024-07-08 | 45481.4125 | 2024-07-08 14:56 | 45481.6222 | 0.1789 | 0.00059237 | 8 | 2416 | Planned | 11.0 Planned Shutdown | Repairing Transformer T136.3
128 |  | PR207 | 11kV Line Peaks Rd | N/A | 449FED | 2024-07-09 | 45482.3368 | 2024-07-09 15:10 | 45482.6319 | 0.53499 | 0.0012588 | 17 | 7225 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and Conductor
129 |  | NJ490 | 11kV Line Wilson Rd | N/A | 219FED | 2024-07-10 | 45483.3417 | 2024-07-10 16:46 | 45483.6986 | 0.94706 | 0.0019993 | 27 | 12790 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and Conductor
130 |  | PR194 | 11kV Line Papakaio Rd | N/A | 219FED | 2024-07-10 | 45483.391 | 2024-07-10 14:22 | 45483.5986 | 0.1107 | 0.00037023 | 5 | 1495 | Planned | 11.0 Planned Shutdown | Replace Cable Connections due to cable shear links corroding
131 |  | NJ487 | 11kV Line Pine Hill Rd | N/A | 449FED | 2024-07-10 | 45483.4944 | 2024-07-10 12:07 | 45483.5049 | 0.0011107 | 7.4047e-05 | 1 | 15 | Planned | 11.0 Planned Shutdown | Install 28m of new UG cable to new SFB tap onto 11kV Pole 29884
132 |  | NJ491 | 11kV Line Wilson Rd | N/A | 219FED | 2024-07-11 | 45484.3417 | 2024-07-11 16:46 | 45484.6986 | 0.55535 | 0.0011107 | 15 | 7500 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and Conductor
133 |  | PR210A | 33/11kV Lines Lake Waitaki to Kurow | N/A | 464FED | 2024-07-11 | 45484.3625 | 2024-07-11 16:18 | 45484.6792 | 1.1143 | 0.0024435 | 33 | 15048 | Planned | 11.0 Planned Shutdown | Tightening
134 |  | F12626 | 33kV Lines Omarama to Ohau | N/A | 2192FED | 2024-07-11 | 45484.4528 | 2024-07-11 11:14 | 45484.4681 | 0.50226 | 0.049241 | 665 | 6783 | Unplanned | 6.0 Wildlife | CB2192 Tripping - Cause Unknown (suspect bird strike)
135 |  | PR210B | 33/11kV Lines Lake Waitaki to Kurow | N/A | 464FED | 2024-07-12 | 45485.3625 | 2024-07-12 16:18 | 45485.6792 | 0.4716 | 0.0024435 | 33 | 6369 | Planned | 11.0 Planned Shutdown | Tightening
136 |  | PR214 | 11kV Line Burnside Rd | N/A | 449FED | 2024-07-15 | 45488.3479 | 2024-07-15 16:24 | 45488.6833 | 0.80348 | 0.0021474 | 29 | 10851 | Planned | 11.0 Planned Shutdown | Trimming Trees between Pole 40345 and 27966a & b
137 |  | NJ496 | 11kV Lines Alma Maheno Rd | N/A | 427FED | 2024-07-15 | 45488.3556 | 2024-07-15 17:22 | 45488.7236 | 2.1977 | 0.0041466 | 56 | 29680 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
138 |  | NJ498 | 11kV Line Gibson Rd | N/A | 219FED | 2024-07-17 | 45490.3576 | 2024-07-17 16:14 | 45490.6764 | 0.40785 | 0.00088856 | 12 | 5508 | Planned | 11.0 Planned Shutdown | Install new NOJA recloser
139 |  | PR212 | 11kV Line Ben Omar Rd | N/A | 424FED | 2024-07-18 | 45491.3542 | 2024-07-18 15:15 | 45491.6354 | 0.41984 | 0.0010367 | 14 | 5670 | Planned | 11.0 Planned Shutdown | Line Shift between poles 29044 and 29037, 6 new poles, replace pole 29307
140 |  | NJ501 | 11kV Line Steward Rd | N/A | 478FED | 2024-07-19 | 45492.3764 | 2024-07-19 09:32 | 45492.3972 | 0.0044428 | 0.00014809 | 2 | 60 | Planned | 11.0 Planned Shutdown | Tighten Crossarm on Pole 21903
141 |  | NJ502 | 11kV Line Steward Rd | N/A | 478FED | 2024-07-19 | 45492.4187 | 2024-07-19 10:36 | 45492.4417 | 0.0073306 | 0.00022214 | 3 | 99 | Planned | 11.0 Planned Shutdown | Resag LV Line between Pole 21898-871969
142 |  | F4737 | 11kV Line Ferry Rd | N/A | 454FED | 2024-07-19 | 45492.5965 | 2024-07-19 14:33 | 45492.6062 | 0.035246 | 0.0025176 | 34 | 476 | Unplanned | 8.0 Defective Equipment | Replace 11kV DDO Pole 22106 (Broken during 11kV Safety Isolation)
143 |  | NJ507A | 33kV / 11kV Line Omarama Twizel | N/A | 491FED | 2024-07-22 | 45495.4028 | 2024-07-22 16:02 | 45495.6681 | 0.14143 | 0.00037023 | 5 | 1910 | Planned | 11.0 Planned Shutdown | Replacing 33KV / 11KV Poles
144 |  | NJ507B | 33kV / 11kV Line Omarama Twizel | N/A | 491FED | 2024-07-23 | 45496.3549 | 2024-07-23 16:39 | 45496.6937 | 0.18067 | 0.00037023 | 5 | 2440 | Planned | 11.0 Planned Shutdown | Replacing 33KV / 11KV Poles
145 |  | NJ505 | 11kV Line Wellington St | N/A | 451FED | 2024-07-23 | 45496.4014 | 2024-07-23 12:50 | 45496.5347 | 0.18482 | 0.00096261 | 13 | 2496 | Planned | 11.0 Planned Shutdown | Install LV Monitor @ Pole 39202, Reconfigure LV & Remove MDI Box
146 |  | F16200 | 11kV Line Livingstone Duntroon Line | N/A | 470FED | 2024-07-23 | 45496.4653 | 2024-07-23 13:51 | 45496.5771 | 0.0311 | 0.0020733 | 28 | 420 | Unplanned | 4.0 Adverse Environment | WDC using Explosives to Remove Cliff near Pole 34376
147 |  | NJ507C | 33kV / 11kV Line Omarama Twizel | N/A | 491FED | 2024-07-24 | 45497.3549 | 2024-07-24 16:20 | 45497.6806 | 0.17364 | 0.00037023 | 5 | 2345 | Planned | 11.0 Planned Shutdown | Replacing 33KV / 11KV Poles
148 |  | NJ512 | 11kV Line Coal Pit Rd | N/A | 449FED | 2024-07-24 | 45497.3826 | 2024-07-24 11:41 | 45497.4868 | 0.1666 | 0.0011107 | 15 | 2250 | Planned | 11.0 Planned Shutdown | Replacing Pole 24829 and install New Transformer
149 |  | NJ509 | Omarama Twizel Rd | N/A | 491FED | 2024-07-25 | 45498.3542 | 2024-07-25 16:18 | 45498.6792 | 0.17327 | 0.00037023 | 5 | 2340 | Planned | 11.0 Planned Shutdown | Replacing 11KV/33KV Poles
150 |  | F16218 F16219 | 529 Tokarahi Duntroon Rd | N/A | 421FED | 2024-07-30 | 45503.0382 | 2024-07-30 13:28 | 45503.5611 | 0.7806 | 0.0010367 | 14 | 10542 | Unplanned | 2.0 Vegetation | Tree through 11Kv Line near Pole #40292
151 |  | F4808 | Weston Ngapara Rd | N/A | 449FED | 2024-07-30 | 45503.8583 | 2024-07-31 00:13 | 45504.009 | 1.668 | 0.018512 | 250 | 22527 | Unplanned | 8.0 Defective Equipment | Broken Insulator at Pole 19833. Tripped R686
152 |  | PR220 | 11kV Line Grant Rd | N/A | 483FED | 2024-08-01 | 45505.3764 | 2024-08-01 12:01 | 45505.5007 | 0.026509 | 0.00014809 | 2 | 358 | Planned | 11.0 Planned Shutdown | Replacing Pole 25787
153 |  | NJ472 | 11kV Line Georgetown Pukeuri Rd | N/A | 456FED | 2024-08-07 | 45511.4389 | 2024-08-07 16:10 | 45511.6736 | 0.025028 | 7.4047e-05 | 1 | 338 | Planned | 11.0 Planned Shutdown | Replace Transformer @ Pole 70960, Replace Crossarms and install LV Cable
154 |  | NJ514 | 11kV Line Black Point Rd | N/A | 444FED | 2024-08-08 | 45512.459 | 2024-08-08 12:54 | 45512.5375 | 0.0083673 | 7.4047e-05 | 1 | 113 | Planned | 11.0 Planned Shutdown | Change Transformer @ Pole 42252
155 |  | F5227 | 18 Airport Rd | N/A | 423FED | 2024-08-12 | 45516.3313 | 2024-08-12 10:07 | 45516.4215 | 0.0096261 | 7.4047e-05 | 1 | 130 | Unplanned | 6.0 Wildlife | Possom Blew 11kV Link @ Pole 29590
156 |  | F5100 F16221 | Brockmans Rd | N/A | 430FED | 2024-08-12 | 45516.4181 | 2024-08-12 15:45 | 45516.6562 | 0.604 | 0.012514 | 169 | 8157 | Unplanned | 8.0 Defective Equipment | (Rotten at Base) Pole 28198 Fell Down in Wind
157 |  | NJ515 | 11kV Line Hampden Palmerston | N/A | 480FED | 2024-08-13 | 45517.3681 | 2024-08-13 14:47 | 45517.616 | 0.47582 | 0.0013328 | 18 | 6426 | Planned | 11.0 Planned Shutdown | Replacing Conductor between Pole 31214-31212 and Replace Crossarms on Pole 31212
158 |  | NJ517 | 11kV Line Parsons Rd | N/A | 430FED | 2024-08-14 | 45518.3799 | 2024-08-14 15:56 | 45518.6639 | 0.6057 | 0.0014809 | 20 | 8180 | Planned | 11.0 Planned Shutdown | Replacing Pole 42475 and Crossarms on Pole 16107, 42471, 39461, 16119, 42472
159 |  | NJ516 | Hampden Palmerston Rd | N/A | 480FED | 2024-08-14 | 45518.4181 | 2024-08-14 11:45 | 45518.4896 | 0.24406 | 0.0023695 | 32 | 3296 | Planned | 11.0 Planned Shutdown | Removing 11KV Links from Pole #41203
160 |  | NJ488 | 11kV Line Ferry Rd | N/A | 435FED | 2024-08-15 | 45519.3681 | 2024-08-15 13:38 | 45519.5681 | 0.021325 | 7.4047e-05 | 1 | 288 | Planned | 11.0 Planned Shutdown | Replacing Transformer at Pole 22034
161 |  | NJ518 | 11kV Line Simpson Rd | N/A | 478FED | 2024-08-15 | 45519.375 | 2024-08-15 13:53 | 45519.5785 | 0.4773 | 0.001629 | 22 | 6446 | Planned | 11.0 Planned Shutdown | Replacing Pole 24408 & Various Crossarms
162 |  | NJ532 | 11kV Line Elderslie Rd | N/A | 449FED | 2024-08-16 | 45520.4167 | 2024-08-16 10:56 | 45520.4556 | 0.0082932 | 0.00014809 | 2 | 112 | Planned | 11.0 Planned Shutdown | Remove 11kV Poles 73742 to 73745 and hardware, Remove T2201
163 |  | NJ524 | 33 & 11kV Lines Papakaio Rd | N/A | 457FED | 2024-08-19 | 45523.3535 | 2024-08-19 13:46 | 45523.5736 | 0.35209 | 0.0011107 | 15 | 4755 | Planned | 11.0 Planned Shutdown | Retightening Papakaio Rd 11kV and 33kV
164 |  | F16225/F4759 | 11kV Line Mchenrys Rd | N/A | 413FED | 2024-08-19 | 45523.7368 | 2024-08-19 17:45 | 45523.7396 | 0.0050352 | 0.0012588 | 17 | 68 | Unplanned | 2.0 Vegetation | Tree Branch on 11kV Line near Pole 13235
165 |  | PR226 | 11kV Line Mcphersons Rd | N/A | 454FED | 2024-08-20 | 45524.3694 | 2024-08-20 13:33 | 45524.5646 | 0.70996 | 0.0028138 | 38 | 9588 | Planned | 11.0 Planned Shutdown | Replacing 11kV Pole 22349 and installing 3 x DDOs 30Amp links crucifix with Las
166 |  | NJ522 | 11kV Line Devils Bridge Rd | N/A | 430FED | 2024-08-20 | 45524.3764 | 2024-08-20 12:07 | 45524.5049 | 0.041096 | 0.00022214 | 3 | 555 | Planned | 11.0 Planned Shutdown | Replace LV Pole pole 39990P & LV Cross arm @ Pole 39478
167 |  | F16227/F4815 | 11kV Line Mcpherson Rd | N/A | 454FED | 2024-08-21 | 45525.5639 | 2024-08-21 15:37 | 45525.6507 | 0.064791 | 0.00051833 | 7 | 875 | Unplanned | 2.0 Vegetation | Tree Branch on 11kV Line near Pole 73422
168 |  | NJ527 | 11kV Line Jardine Rd | N/A | 219FED | 2024-08-23 | 45527.3972 | 2024-08-23 12:30 | 45527.5208 | 0.21088 | 0.0011847 | 16 | 2848 | Planned | 11.0 Planned Shutdown | Retightening Jardine Rd 11kV and 33kV
169 |  | NJ489 | 11kV Line Settlement Rd | N/A | 411FED | 2024-08-23 | 45527.4201 | 2024-08-23 11:19 | 45527.4715 | 0.032877 | 0.00044428 | 6 | 444 | Planned | 11.0 Planned Shutdown | Tighten & double nut 11kV pole 11378 carry out other maintenance
170 |  | F4858 | 275 Homestead Rd | N/A | 430FED | 2024-08-28 | 45532.9257 | 2024-08-28 22:50 | 45532.9514 | 0.0082192 | 0.00022214 | 3 | 111 | Unplanned | 6.0 Wildlife | Blown HV Fuses - Possom
171 |  | NJ530 | 11kV Line Warepa Rd | N/A | 219FED | 2024-08-29 | 45533.3576 | 2024-08-29 15:52 | 45533.6611 | 0.16179 | 0.00037023 | 5 | 2185 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
172 |  | NJ541 | 11kV Line Georgetown Pukeuri Rd | N/A | 444FED | 2024-08-30 | 45534.4236 | 2024-08-30 14:59 | 45534.6243 | 0.021399 | 7.4047e-05 | 1 | 289 | Planned | 11.0 Planned Shutdown | Installing LV Monitoring
173 |  | F5230 | 18 Airport Rd | N/A | 423FED | 2024-08-30 | 45534.5514 | 2024-08-30 14:13 | 45534.5924 | 0.2097 | 0.0035542 | 48 | 2832 | Unplanned | 8.0 Defective Equipment | Replacing Faulty Blown LA at Pole 29590
174 |  | PR229 | 11kV Line Roundhill Rd | N/A | 428FED | 2024-09-02 | 45537.3778 | 2024-09-02 12:15 | 45537.5104 | 0.48086 | 0.0025176 | 34 | 6494 | Planned | 11.0 Planned Shutdown | Replace Pole 26317, Replace 3 x DDOs on pole 26319. Replace SA on Pole 25153
175 |  | F4859 | State Highway 1 Herbert Hampden Rd | N/A | 479FED | 2024-09-02 | 45537.9972 | 2024-09-03 13:33 | 45538.5646 | 1.5359 | 0.030433 | 411 | 20742 | Unplanned | 2.0 Vegetation | Tree Through the 11kV Lines at Pole 28349
176 |  | PR230 | 11kV Line Robbs Crossing Rd | N/A | 428FED | 2024-09-03 | 45538.3715 | 2024-09-03 15:49 | 45538.659 | 0.5518 | 0.0013328 | 18 | 7452 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
177 |  | NJ538 | 11kV Line Airedale Rd | N/A | 429FED | 2024-09-04 | 45539.3542 | 2024-09-04 15:50 | 45539.6597 | 1.3032 | 0.0029619 | 40 | 17600 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
178 |  | NJ539 | 11kV Line Airedale Rd | N/A | 429FED | 2024-09-05 | 45540.3569 | 2024-09-05 10:20 | 45540.4306 | 0.0078489 | 7.4047e-05 | 1 | 106 | Planned | 11.0 Planned Shutdown | Replace 15kVA transformer on 11kV Pole 15824
179 |  | PR238 | 11kV Line Waiora Rd | N/A | 415FED | 2024-09-05 | 45540.3764 | 2024-09-05 11:43 | 45540.4882 | 0.023843 | 0.00014809 | 2 | 322 | Planned | 11.0 Planned Shutdown | Replace 2 x DDOs Links on pole 12607. Replace SA on pole 12604
180 |  | NJ513 | 11kV Line Falconers Rd | N/A | 479FED | 2024-09-05 | 45540.4389 | 2024-09-05 12:08 | 45540.5056 | 0.014217 | 0.00014809 | 2 | 192 | Planned | 11.0 Planned Shutdown | Install LV Monitor onto 11kV Pole 39875
181 |  | NJ540 | 11kV Line Airedale Rd | N/A | 429FED | 2024-09-05 | 45540.525 | 2024-09-05 13:46 | 45540.5736 | 0.0051833 | 7.4047e-05 | 1 | 70 | Planned | 11.0 Planned Shutdown | Replace 15kVA transformer on 11kV Pole 15860
182 |  | PR239A | 11kV Line Kuriheka Rd | N/A | 415FED | 2024-09-06 | 45541.3618 | 2024-09-06 15:01 | 45541.6257 | 0.16883 | 0.00044428 | 6 | 2280 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
183 |  | PR239B | 11kV Line Kuriheka Rd | N/A | 415FED | 2024-09-09 | 45544.3667 | 2024-09-09 16:01 | 45544.6674 | 0.19237 | 0.00044428 | 6 | 2598 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
184 |  | F4867 | 47 Teaneaki Settlement Rd | N/A | 449FED | 2024-09-09 | 45544.4694 | 2024-09-09 11:42 | 45544.4875 | 0.0038504 | 0.00014809 | 2 | 52 | Unplanned | 8.0 Defective Equipment | No Power. LV service wrapped around itself in wind
185 |  | F5267 | 151 Earthquakes Rd | N/A | 470FED | 2024-09-09 | 45544.6625 | 2024-09-09 16:50 | 45544.7014 | 0.016883 | 0.00022214 | 3 | 228 | Unplanned | 2.0 Vegetation | Branch on Line at Pole 12655 - Blown HV Fuses
186 |  | F16238/16239 | Twizel Omarama Rd | N/A | 491FED | 2024-09-10 | 45545.025 | 2024-09-12 13:52 | 45547.5778 | 0.27708 | 0.0026657 | 36 | 3742 | Unplanned | 8.0 Defective Equipment | 11kV Cable Fault at Pole 11174
187 |  | PR246 | 11kV Line Burnside Rd | N/A | 451FED | 2024-09-10 | 45545.3604 | 2024-09-10 15:41 | 45545.6535 | 0.093743 | 0.00022214 | 3 | 1266 | Planned | 11.0 Planned Shutdown | String Third Phase from Pole 27795 to 27807
188 |  | NJ556 | 33kV Line Otematata Substation | N/A | 524FED | 2024-09-10 | 45545.3826 | 2024-09-10 16:14 | 45545.6764 | 0.21925 | 0.00051833 | 7 | 2961 | Planned | 11.0 Planned Shutdown | Installing new Pole E and Replacing Conductor between Pole E & Pole C
189 |  | NJ543 | 11kV Line Fortification Rd | N/A | 427FED | 2024-09-10 | 45545.3854 | 2024-09-10 13:00 | 45545.5417 | 0.066642 | 0.00029619 | 4 | 900 | Planned | 11.0 Planned Shutdown | Install new LV Span from Poles 20850 to 36278
190 |  | F16240 | 11kV Line Burnside Rd | N/A | 451FED | 2024-09-11 | 45546.3576 | 2024-09-11 11:41 | 45546.4868 | 0.013773 | 7.4047e-05 | 1 | 186 | Planned | 11.0 Planned Shutdown | Change Transformer on Pole 27806
191 |  | NJ548 | 11kV Line Twizel Omarama Rd | N/A | 492FED | 2024-09-11 | 45546.3958 | 2024-09-11 11:37 | 45546.484 | 0.094039 | 0.00074047 | 10 | 1270 | Planned | 11.0 Planned Shutdown | Remove Temp Links on Pole 39766
192 |  | PR234 | 11kV Line Manse Rd | N/A | 411FED | 2024-09-11 | 45546.3972 | 2024-09-11 13:38 | 45546.5681 | 0.036431 | 0.00014809 | 2 | 492 | Planned | 11.0 Planned Shutdown | Install new SFB
193 |  | F16242 | 11kV Line Prydes Gully Rd | N/A | 421FED | 2024-09-11 | 45546.6958 | 2024-09-11 16:48 | 45546.7 | 0.039985 | 0.0066642 | 90 | 540 | Unplanned | 8.0 Defective Equipment | ABS1176 Springside West Arcing (inspect)
194 |  | F16243 | 11kV Line Redcastle Rd | N/A | 430FED | 2024-09-11 | 45546.8049 | 2024-09-11 21:00 | 45546.875 | 0.29167 | 0.0028878 | 39 | 3939 | Unplanned | 5.0 Third party Interference | Car vs Pole
195 |  | NJ560 | 11kV Line Ferry Rd | N/A | 435FED | 2024-09-16 | 45551.4181 | 2024-09-16 12:18 | 45551.5125 | 0.01007 | 7.4047e-05 | 1 | 136 | Planned | 11.0 Planned Shutdown | Install LV Monitor
196 |  | PR250 | 11kV Line Macdonalds Rd | N/A | 454FED | 2024-09-17 | 45552.4181 | 2024-09-17 11:58 | 45552.4986 | 0.18897 | 0.001629 | 22 | 2552 | Planned | 11.0 Planned Shutdown | Transformer Upgrade
197 |  | PR249 | 11kV Line Jessicas Lane | N/A | 430FED | 2024-09-18 | 45553.4201 | 2024-09-18 13:35 | 45553.566 | 0.062199 | 0.00029619 | 4 | 840 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms
198 |  | F15993 | Kakanui Rd | N/A | 416FED | 2024-09-20 | 45555.9951 | 2024-09-21 02:50 | 45556.1181 | 0.95676 | 0.0054054 | 73 | 12921 | Unplanned | 5.0 Third party Interference | Car vs Pole
199 |  | F16247 | Milne Rd | N/A | 413FED | 2024-09-24 | 45559.45 | 2024-09-24 11:28 | 45559.4778 | 0.071085 | 0.0017771 | 24 | 960 | Unplanned | 8.0 Defective Equipment | Broken Binder and loose Bolts
200 |  | PR254 | 11kV Line Waianakarua Rd | N/A | 479FED | 2024-09-25 | 45560.3632 | 2024-09-25 12:21 | 45560.5146 | 0.032284 | 0.00014809 | 2 | 436 | Planned | 11.0 Planned Shutdown | Repair 11kV cable term on pole 39426
201 |  | F16250 | 11kV Line Livingstone st Duntroon | N/A | 470FED | 2024-09-25 | 45560.3632 | 2024-09-27 13:40 | 45562.5694 | 0.4876 | 0.0028138 | 38 | 6585 | Unplanned | 5.0 Third party Interference | Customer cut tree down threw line, started small fire. Damaged poles and equipment
202 |  | F16249 | Settlement Rd | N/A | 470FED | 2024-09-25 | 45560.4125 | 2024-09-25 10:17 | 45560.4285 | 0.010218 | 0.00044428 | 6 | 138 | Unplanned | 6.0 Wildlife | Remove Bird Nest
203 |  | NJ574 | 11kV Line Gray Rd | N/A | 454FED | 2024-09-27 | 45562.3861 | 2024-09-27 11:46 | 45562.4903 | 0.099963 | 0.00066642 | 9 | 1350 | Planned | 11.0 Planned Shutdown | Remove 11kV Span from Poles 23492 & 21916
204 |  | PR261 | 11kV Line Wainakarua Rd | N/A | 479FED | 2024-09-30 | 45565.3722 | 2024-09-30 09:39 | 45565.4021 | 0.090041 | 0.0017771 | 24 | 1216 | Planned | 11.0 Planned Shutdown | Repair 11kV Cable term on Pole 30813
205 |  | NJ541 | 11kV Line Georgetown Pukeuri Rd | N/A | 444FED | 2024-09-30 | 45565.3743 | 2024-09-30 11:41 | 45565.4868 | 0.011996 | 7.4047e-05 | 1 | 162 | Planned | 11.0 Planned Shutdown | Installing LV Monitoring on 11kV pole 23675 onto Tx2518
206 |  | NJ547 | Twizel Omarama Rd | N/A | 491FED | 2024-10-01 | 45566.375 | 2024-10-01 11:59 | 45566.4993 | 0.066272 | 0.00037023 | 5 | 895 | Planned | 11.0 Planned Shutdown | Install 33kV clamp top insulators and install double arms on 33kV poles 36251 & 21241
207 |  | NJ525 & PI168 | Papakaio Rd | N/A | 491FED | 2024-10-02 | 45567.3972 | 2024-10-02 13:02 | 45567.5431 | 0.57534 | 0.0027397 | 37 | 7770 | Planned | 11.0 Planned Shutdown | TIghtening
208 |  | F16455 | 11kV Line Milne Rd | N/A | 413FED | 2024-10-02 | 45567.4604 | 2024-10-02 13:13 | 45567.5507 | 0.038504 | 0.00029619 | 4 | 520 | Unplanned | 8.0 Defective Equipment | Tighten centre bolting at Pole 29349
209 |  | NJ578A | Aitcheson Rd | N/A | 219FED | 2024-10-03 | 45568.3542 | 2024-10-03 11:39 | 45568.4854 | 0.72773 | 0.0038504 | 52 | 9828 | Planned | 11.0 Planned Shutdown | Tightening
210 |  | NJ578B | Aitcheson Rd | N/A | 219FED | 2024-10-04 | 45569.3549 | 2024-10-04 10:54 | 45569.4542 | 0.55061 | 0.0038504 | 52 | 7436 | Planned | 11.0 Planned Shutdown | Tightening
211 |  | PR262 | 11kV Line Uxbridge Rd | N/A | 444FED | 2024-10-09 | 45574.5687 | 2024-10-09 17:39 | 45574.7354 | 0.017771 | 7.4047e-05 | 1 | 240 | Planned | 11.0 Planned Shutdown | Reconfigure 11kV and install Replacement Groundmount
212 |  | PR264 | 11kV Line Kauru Hill Rd | N/A | 415FED | 2024-10-10 | 45575.3472 | 2024-10-10 15:25 | 45575.6424 | 1.9197 | 0.0045168 | 61 | 25925 | Planned | 11.0 Planned Shutdown | Replace Poles and Hardware
213 |  | F16457 | Wilson Rd | N/A | 219FED | 2024-10-11 | 45576.2576 | 2024-10-11 08:12 | 45576.3417 | 0.41733 | 0.0066642 | 90 | 5636 | Unplanned | 8.0 Defective Equipment | 11kV Wire Down Pole 41569
214 |  | PR269 | 11kV Line Roundhill Rd | N/A | 428FED | 2024-10-14 | 45579.3986 | 2024-10-14 14:49 | 45579.6174 | 0.39652 | 0.0012588 | 17 | 5355 | Planned | 11.0 Planned Shutdown | Replacing Transformer @ Pole 26368
215 |  | F4881A | 151 Earthquakes Rd | N/A | 470FED | 2024-10-14 | 45579.5319 | 2024-10-14 14:23 | 45579.5993 | 0.021548 | 0.00022214 | 3 | 291 | Unplanned | 6.0 Wildlife | Duck Blew 11kV Links at Pole 12653 and Pole 73776
216 |  | NJ594A | 11kV Line St Helens Rd | N/A | 451FED | 2024-10-16 | 45581.3757 | 2024-10-16 14:00 | 45581.5833 | 0.35424 | 0.0011847 | 16 | 4784 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms, Conductor and Install Transformer
217 |  | PR267 | 11kV Line Lake Ohau Rd | N/A | 490FED | 2024-10-16 | 45581.4111 | 2024-10-16 16:18 | 45581.6792 | 0.34217 | 0.00088856 | 12 | 4621 | Planned | 11.0 Planned Shutdown | Removing Pole 19500B and Replacing ABS1232
218 |  | PR270 | Lake Ohau Rd | N/A | 490FED | 2024-10-17 | 45582.3549 | 2024-10-17 16:28 | 45582.6861 | 0.28256 | 0.00059237 | 8 | 3816 | Planned | 11.0 Planned Shutdown | Tighten Between ABS1111 and Pole 35705
219 |  | PR227 | Dunrobin Rd | N/A | 486FED | 2024-10-17 | 45582.3583 | 2024-10-17 15:11 | 45582.6326 | 0.32173 | 0.00081451 | 11 | 4345 | Planned | 11.0 Planned Shutdown | Replacing Pole 16477 & Pole 16481 and install Transformers
220 |  | NJ594B | 11kV Line St Helens Rd | N/A | 451FED | 2024-10-17 | 45582.3771 | 2024-10-17 14:03 | 45582.5854 | 0.35542 | 0.0011847 | 16 | 4800 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms, Conductor and Install Transformer
221 |  | F16456 | Ohau Substation | N/A | 2192FED | 2024-10-19 | 45584.009 | 2024-10-19 00:41 | 45584.0285 | 0.31396 | 0.048204 | 651 | 4240 | Unplanned | 9.0 Cause Unknown | Recloser R818 Tripped
222 |  | PR153 | 11kV Line Island Stream Rd | N/A | 415FED | 2024-10-21 | 45586.3333 | 2024-10-21 14:32 | 45586.6056 | 0.028804 | 7.4047e-05 | 1 | 389 | Planned | 11.0 Planned Shutdown | Replacing 11kV Condutor between Pole 25948 - Pole 26489
223 |  | PR271 | Lake Ohau Rd | N/A | 490FED | 2024-10-21 | 45586.375 | 2024-10-21 16:29 | 45586.6868 | 3.5913 | 0.0085154 | 115 | 48500 | Planned | 11.0 Planned Shutdown | Tighten between ABS1022 and ABS1570 and Install 11kV Links at Pole 19496 & 40451
224 |  | PR272 | 11kV Line Ohau Rd | N/A | 490FED | 2024-10-22 | 45587.3597 | 2024-10-22 13:01 | 45587.5424 | 0.2134 | 0.00081451 | 11 | 2882 | Planned | 11.0 Planned Shutdown | Tigthtens between ABS1570 and 11kV Links Pole 35915
225 |  | PR274 | 11kV Line Dasher Rd | N/A | 415FED | 2024-10-23 | 45588.3493 | 2024-10-23 14:13 | 45588.5924 | 0.025916 | 7.4047e-05 | 1 | 350 | Planned | 11.0 Planned Shutdown | Replace Pole 19896 and Replace Transformer
226 |  | NJ596A | Henburn Rd | N/A | 424FED | 2024-10-23 | 45588.3549 | 2024-10-23 16:20 | 45588.6806 | 0.20837 | 0.00044428 | 6 | 2814 | Planned | 11.0 Planned Shutdown | Replace poles, Crossarms and Conductor from pole 14547 to Pole 40230
227 |  | NJ597 | 11kV Line Quailburn Rd | N/A | 424FED | 2024-10-24 | 45589.3549 | 2024-10-24 14:22 | 45589.5986 | 0.15594 | 0.00044428 | 6 | 2106 | Planned | 11.0 Planned Shutdown | Relocate ABS1200 and Replace Conductor between Pole 14547 and Pole 10712
228 |  | PR277 | 11kV Line Tilverstowe Rd | N/A | 421FED | 2024-10-24 | 45589.4264 | 2024-10-24 14:53 | 45589.6201 | 0.44894 | 0.00311 | 42 | 6063 | Planned | 11.0 Planned Shutdown | Replace Transformer @ Pole 37375 and install 3rd DDO
229 |  | F5284 | 3516 Kurow Duntroon Rd | N/A | 470FED | 2024-10-25 | 45590.2854 | 2024-10-25 08:00 | 45590.3333 | 0.020437 | 0.00029619 | 4 | 276 | Unplanned | 6.0 Wildlife | Rodents blew 11kV Links Pole 38844
230 |  | NJ596B | Henburn Rd | N/A | 424FED | 2024-10-25 | 45590.3556 | 2024-10-25 13:59 | 45590.5826 | 0.14528 | 0.00044428 | 6 | 1962 | Planned | 11.0 Planned Shutdown | Replace poles, Crossarms and Conductor from pole 14547 to Pole 40230
231 |  | F5285 | Ohau | N/A | 490FED | 2024-10-26 | 45591.6035 | 2024-10-27 14:26 | 45592.6014 | 2.196 | 0.001555 | 21 | 29657 | Unplanned | 3.0 Adverse Weather | Broken Conductor @ Pole #874103
232 |  | F4845 | 1490 Birchwood Rd | N/A | 424FED | 2024-10-26 | 45591.6264 | 2024-10-27 14:12 | 45592.5917 | 0.63073 | 0.00096261 | 13 | 8518 | Unplanned | 2.0 Vegetation | Tree Through 11Kv Line
233 |  | F4847 F30330 | 162 Boundary Creek Rd | N/A | 432FED | 2024-10-27 | 45592.434 | 2024-10-27 11:02 | 45592.4597 | 0.0054795 | 0.00014809 | 2 | 74 | Unplanned | 2.0 Vegetation | Tree Branch through LV Span
234 |  | NJ596C | Henburn Rd | N/A | 424FED | 2024-10-29 | 45594.3854 | 2024-10-29 16:17 | 45594.6785 | 0.18749 | 0.00044428 | 6 | 2532 | Planned | 11.0 Planned Shutdown | Replace poles, Crossarms and Conductor from pole 14547 to Pole 40230
235 |  | PR280 | 11kV Line Danseys Pass Rd | N/A | 421FED | 2024-10-30 | 45595.3431 | 2024-10-30 15:02 | 45595.6264 | 0.4856 | 0.0014809 | 20 | 6558 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms and Tightening
236 |  | NJ596D | Henburn Rd | N/A | 424FED | 2024-10-30 | 45595.3549 | 2024-10-30 16:11 | 45595.6743 | 0.20437 | 0.00044428 | 6 | 2760 | Planned | 11.0 Planned Shutdown | Replace poles, Crossarms and Conductor from pole 14547 to Pole 40230
237 |  | NJ596E | Henburn Rd | N/A | 424FED | 2024-10-31 | 45596.3542 | 2024-10-31 13:40 | 45596.5694 | 0.13773 | 0.00044428 | 6 | 1860 | Planned | 11.0 Planned Shutdown | Replace poles, Crossarms and Conductor from pole 14547 to Pole 40230
238 |  | NJ604 | 33kV 11kV Line Omarama Otematata | N/A | 424FED | 2024-10-31 | 45596.3785 | 2024-10-31 15:50 | 45596.6597 | 0.47982 | 0.0011847 | 16 | 6480 | Planned | 11.0 Planned Shutdown | 33kV & 11kV Climbing Patrol
239 |  | F4849 | 280 Reservoir Rd | N/A | 437FED | 2024-10-31 | 45596.6007 | 2024-10-31 15:15 | 45596.6354 | 0.0037023 | 7.4047e-05 | 1 | 50 | Unplanned | 6.0 Wildlife | Rodent Blew 11kV Link @ Pole 32439
240 |  | NJ620 | 11kV Line Birchwood Rd | N/A | 423FED | 2024-11-01 | 45597.3604 | 2024-11-01 13:02 | 45597.5431 | 0.097371 | 0.00037023 | 5 | 1315 | Planned | 11.0 Planned Shutdown | Replace 11kV Poles 37168 & 37171
241 |  | NJ612 | 11kV Line Prohibition Rd | N/A | 424FED | 2024-11-04 | 45600.359 | 2024-11-04 15:15 | 45600.6354 | 0.55994 | 0.0014069 | 19 | 7562 | Planned | 11.0 Planned Shutdown | Climbing Patrol and retighening
242 |  | F5379 | Cochranes Rd | N/A | 413FED | 2024-11-05 | 45601.6083 | 2024-11-07 14:57 | 45603.6229 | 0.21037 | 7.4047e-05 | 1 | 2841 | Unplanned | 8.0 Defective Equipment | 11kV Floating Wires and Replace Pole 10912
243 |  | F4903 | 17 Pringles Gully Rd | N/A | 421FED | 2024-11-06 | 45602.3125 | 2024-11-06 09:47 | 45602.4076 | 0.010144 | 7.4047e-05 | 1 | 137 | Unplanned | 6.0 Wildlife | Possom Blew 11kV Links @ Pole 22822
244 |  | NJ607A | Maheno Kakanui Rd | N/A | 416FED | 2024-11-06 | 45602.3771 | 2024-11-06 15:56 | 45602.6639 | 0.12233 | 0.00029619 | 4 | 1652 | Planned | 11.0 Planned Shutdown | Replace Pole 30612 and install new R712 West Kakanui
245 |  | F5300 | 45 Baghdad | N/A | 480FED | 2024-11-06 | 45602.8222 | 2024-11-06 21:05 | 45602.8785 | 0.023991 | 0.00029619 | 4 | 324 | Unplanned | 8.0 Defective Equipment | No Power 11kV Link Corroded
246 |  | NJ610 | Argyle St | N/A | 427FED | 2024-11-07 | 45603.3618 | 2024-11-07 18:14 | 45603.7597 | 1.0607 | 0.0018512 | 25 | 14325 | Planned | 11.0 Planned Shutdown | Replacing Pole 28703 and Pole 28702 and ABS1105
247 |  | NJ607B | Maheno Kakanui Rd | N/A | 416FED | 2024-11-07 | 45603.3729 | 2024-11-07 14:27 | 45603.6021 | 0.097742 | 0.00029619 | 4 | 1320 | Planned | 11.0 Planned Shutdown | Replace Pole 30612 and install new R712 West Kakanui
248 |  | F16468 | Brookstead Rd | N/A | 444FED | 2024-11-07 | 45603.3729 | 2024-11-07 14:27 | 45603.6021 | 0.33388 | 0.0056275 | 76 | 4509 | Unplanned | 5.0 Third party Interference | Truck Against 11kV Line near Pole 15986
249 |  | PR284 | Dunrobin Rd | N/A | 486FED | 2024-11-12 | 45608.3333 | 2024-11-12 15:32 | 45608.6472 | 0.60244 | 0.0013328 | 18 | 8136 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms & Tightening
250 |  | NJ618A | 11kV Line Waianakarua Rd | N/A | 479FED | 2024-11-12 | 45608.3625 | 2024-11-12 15:34 | 45608.6486 | 0.24339 | 0.00059237 | 8 | 3287 | Planned | 11.0 Planned Shutdown | Replacing ABS1004 with TSW1720
251 |  | F4953 | 507 Whitestone Five Forks Rd | N/A | 451FED | 2024-11-13 | 45609.3375 | 2024-11-13 09:30 | 45609.3958 | 0.01866 | 0.00022214 | 3 | 252 | Unplanned | 6.0 Wildlife | Rodents Blew 11kV links Pole 39227
252 |  | PR285 | 11kV Line Dunrobin Rd | N/A | 486FED | 2024-11-13 | 45609.3403 | 2024-11-13 14:46 | 45609.6153 | 0.20007 | 0.00051833 | 7 | 2702 | Planned | 11.0 Planned Shutdown | Replacing Poles, Crossarms & Double Nutting
253 |  | NJ618B | 11kV Line Waianakarua Rd | N/A | 479FED | 2024-11-13 | 45609.3583 | 2024-11-13 13:41 | 45609.5701 | 0.18016 | 0.00059237 | 8 | 2433 | Planned | 11.0 Planned Shutdown | Replacing ABS1004 with TSW1720
254 |  | PR288 | Hedley Rd | N/A | 472FED | 2024-11-15 | 45611.3382 | 2024-11-15 17:59 | 45611.7493 | 0.057386 | 0.0021474 | 29 | 775 | Planned | 11.0 Planned Shutdown | Installing New Pole N1 & N2
255 |  | F16474 | Omarama Sub | N/A | 2192FED | 2024-11-15 | 45611.5639 | 2024-11-15 13:41 | 45611.5701 | 0.30056 | 0.035394 | 478 | 4059 | Unplanned | 9.0 Cause Unknown | R808 Tripped
256 |  | PI185 | Industrial Park RMU | N/A | 438FED | 2024-11-17 | 45613.6 | 2024-11-17 15:00 | 45613.625 | 0.071973 | 0.0019993 | 27 | 972 | Planned | 11.0 Planned Shutdown | Changing 11kV Fuses
257 |  | PI184 | Hedley Rd | N/A | 472FED | 2024-11-19 | 45615.341 | 2024-11-19 17:59 | 45615.7493 | 0.062273 | 0.0021474 | 29 | 841 | Planned | 11.0 Planned Shutdown | Removing 11kV Overhead Lines between Poler N1 & N2 and Replacing with 11kV Cable
258 |  | NJ603 | Broken Hut Rd | N/A | 423FED | 2024-11-19 | 45615.375 | 2024-11-19 13:15 | 45615.5521 | 0.2077 | 0.00081451 | 11 | 2805 | Planned | 11.0 Planned Shutdown | Climbing Patrol & Tightens
259 |  | F16476 | Boundary Creek Rd | N/A | 432FED | 2024-11-21 | 45617.4035 | 2024-11-21 10:31 | 45617.4382 | 0.0074047 | 0.00014809 | 2 | 100 | Unplanned | 2.0 Vegetation | Erecting LV Wires 2 Pole 33534
260 |  | PI188 | Twizel Omarama Rd | N/A | 424FED | 2024-11-22 | 45618.3333 | 2024-11-22 14:01 | 45618.584 | 0.88145 | 0.0025176 | 34 | 11904 | Unplanned | 8.0 Defective Equipment | Replacing ABS1193 & Pole 29524
261 |  | NJ626 | Livingstone -Duntroon Rd | N/A | 421FED | 2024-11-25 | 45621.3556 | 2024-11-25 15:35 | 45621.6493 | 0.93965 | 0.0022214 | 30 | 12690 | Planned | 11.0 Planned Shutdown | Climbing Patrol & Tightening
262 |  | NJ627 | Livingstone Duntroon Rd | N/A | 421FED | 2024-11-26 | 45622.3562 | 2024-11-26 15:31 | 45622.6465 | 0.21666 | 0.00051833 | 7 | 2926 | Planned | 11.0 Planned Shutdown | Climbing Patrol & Tightening
263 |  | NJ636 | Otematata Omarama Rd | N/A | 425FED | 2024-11-28 | 45624.3569 | 2024-11-28 15:40 | 45624.6528 | 0.53625 | 0.0012588 | 17 | 7242 | Planned | 11.0 Planned Shutdown | Climbing Patrol & Tightening
264 |  | PR295 | Gillies Foundry Halo | N/A | 407FED | 2024-11-30 | 45626.3389 | 2024-12-01 11:36 | 45627.4833 | 0.12203 | 7.4047e-05 | 1 | 1648 | Planned | 11.0 Planned Shutdown | Replacing Gillies Foundary Halo
265 |  | F16481 | Omarama Ohau Ruataniwha | N/A | 2192FED | 2024-12-01 | 45627.5931 | 2024-12-01 16:14 | 45627.6764 | 0.489 | 0.049537 | 669 | 6604 | Unplanned | 6.0 Wildlife | Bird @ ABS3370 Caused CB2192 Twizel to Trip[
266 |  | NJ645 | Omarama Twizel Rd | N/A | 424FED | 2024-12-03 | 45629.4174 | 2024-12-03 13:09 | 45629.5479 | 0.20881 | 0.0011107 | 15 | 2820 | Planned | 11.0 Planned Shutdown | Retighten & Patrol Between Pole 36198 - Pole 29625
267 |  | F5403 | 1232 Weston Ngapara Rd | N/A | 449FED | 2024-12-06 | 45632.541 | 2024-12-06 15:59 | 45632.666 | 0.013328 | 7.4047e-05 | 1 | 180 | Unplanned | 9.0 Cause Unknown | Blown DDO at Pole 41331
268 |  | F16484 | Dansey Pass Rd | N/A | 421FED | 2024-12-08 | 45634.8132 | 2024-12-09 12:18 | 45635.5125 | 0.32581 | 0.0013328 | 18 | 4400 | Unplanned | 2.0 Vegetation | Tree through 11kV line between Pole 22880 - 22879
269 |  | NJ651 | Livingston Duntroon Rd | N/A | 473FED | 2024-12-09 | 45635.3958 | 2024-12-09 10:40 | 45635.4444 | 0.0051833 | 7.4047e-05 | 1 | 70 | Planned | 11.0 Planned Shutdown | Raising and Terminating LV Cable & Install New LV Fuse Base
270 |  | PR302 | Omarama Twizel Rd | N/A | 424FED | 2024-12-09 | 45635.4375 | 2024-12-09 11:59 | 45635.4993 | 0.098852 | 0.0011107 | 15 | 1335 | Planned | 11.0 Planned Shutdown | Replacing Pole 29537
271 |  | NJ652A | 11kV Line Birchwood Rd | N/A | 423FED | 2024-12-11 | 45637.3389 | 2024-12-11 18:07 | 45637.7549 | 0.044354 | 7.4047e-05 | 1 | 599 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms
272 |  | F16486 | 1183 Wainakarua Rd | N/A | 479FED | 2024-12-11 | 45637.6285 | 2024-12-11 17:24 | 45637.725 | 0.020585 | 0.00014809 | 2 | 278 | Unplanned | 8.0 Defective Equipment | Replacing LV Fuse Base @ Pole 70549
273 |  | NJ652B | 11kV Line Birchwood Rd | N/A | 423FED | 2024-12-12 | 45638.3403 | 2024-12-12 18:29 | 45638.7701 | 0.036949 | 7.4047e-05 | 1 | 499 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms
274 |  | PR295-1 | Gillies Foundry Halo | N/A | 407FED | 2024-12-12 | 45638.4 | 2024-12-12 13:32 | 45638.5639 | 0.019696 | 7.4047e-05 | 1 | 266 | Planned | 11.0 Planned Shutdown | Completing Replacement of Gillies Foundry Halo
275 |  | 2487PI | Omarama Twizel Rd | N/A | 492FED | 2024-12-12 | 45638.4424 | 2024-12-12 12:16 | 45638.5111 | 0.087967 | 0.00088856 | 12 | 1188 | Unplanned | 8.0 Defective Equipment | Resage Conductors between Pole 21086 - Pole 41708
276 |  | NJ652C | 11kV Line Birchwood Rd | N/A | 423FED | 2024-12-13 | 45639.3389 | 2024-12-13 11:32 | 45639.4806 | 0.015106 | 7.4047e-05 | 1 | 204 | Planned | 11.0 Planned Shutdown | Replacing Poles and Crossarms
277 |  | PR298 | Herbert Hampden Rd | N/A | 479FED | 2024-12-13 | 45639.3729 | 2024-12-13 10:59 | 45639.4576 | 0.036135 | 0.00029619 | 4 | 488 | Planned | 11.0 Planned Shutdown | Reconfigure LV lines to 3 phase @ Pole 14222
278 |  | NJ653 | Birchwood Rd | N/A | 423FED | 2024-12-16 | 45642.3986 | 2024-12-16 14:23 | 45642.5993 | 0.107 | 0.00037023 | 5 | 1445 | Planned | 11.0 Planned Shutdown | Replacing Pole 37169 and installing transformer & maintenance
279 |  | PR288-1 | Hedley Rd | N/A | 472FED | 2024-12-16 | 45642.4146 | 2024-12-16 13:51 | 45642.5771 | 0.021474 | 0.0020733 | 28 | 290 | Planned | 11.0 Planned Shutdown | Replacing Stays @ New Pole N1 & N2
280 |  | NJ654A | Birchwood Rd | N/A | 423FED | 2024-12-17 | 45643.3347 | 2024-12-17 15:14 | 45643.6347 | 0.38386 | 0.00088856 | 12 | 5184 | Planned | 11.0 Planned Shutdown | Replacing Poles
281 |  | PR306 | Milne Rd Haka Valley | N/A | 413FED | 2024-12-17 | 45643.5417 | 2024-12-17 15:54 | 45643.6625 | 0.47671 | 0.0027397 | 37 | 6438 | Planned | 11.0 Planned Shutdown | Trim Trees between Pole 39140 - 72757 and Replace Centre Bolt @ Pole 14493
282 |  | NJ654B | Birchwood Rd | N/A | 423FED | 2024-12-18 | 45644.3347 | 2024-12-18 15:00 | 45644.625 | 0.37142 | 0.00088856 | 12 | 5016 | Planned | 11.0 Planned Shutdown | Replacing Poles
283 |  | PR307 | Dansey Pass Rd | N/A | 421FED | 2024-12-18 | 45644.359 | 2024-12-18 14:56 | 45644.6222 | 0.3087 | 0.00081451 | 11 | 4169 | Planned | 11.0 Planned Shutdown | Tree Removal Between Pole 22879 - Pole 22881
284 |  | PR305 | Tenby St Moeraki | N/A | 480FED | 2024-12-18 | 45644.3778 | 2024-12-18 12:13 | 45644.509 | 0.083969 | 0.00044428 | 6 | 1134 | Planned | 11.0 Planned Shutdown | Replacing Transformer on Pole 39256 & Installing NEW SFB from Pole 18471
285 |  | F5411 | Hurstlea Rd | N/A | 413FED | 2024-12-18 | 45644.4708 | 2024-12-18 11:45 | 45644.4896 | 0.011996 | 0.00044428 | 6 | 162 | Unplanned | 8.0 Defective Equipment | Replacing Clamp Top Insulator at Pole 18106
286 |  | NJ655 | Birchwood Rd | N/A | 423FED | 2024-12-19 | 45645.3333 | 2024-12-19 15:28 | 45645.6444 | 1.0573 | 0.0023695 | 32 | 14279 | Planned | 11.0 Planned Shutdown | Replacing Various poles and Trimming Trees beteen Pole 15181 - Pole 40257
287 |  | F4974 | Arundel St | N/A | 445FED | 2024-12-25 | 45651.0972 | 2024-12-25 02:26 | 45651.1014 | 0.412 | 0.015846 | 214 | 5564 | Unplanned | 5.0 Third party Interference | Car vs Pole 32272
288 |  | F4868 | 480 Corbett Rd | N/A | 435FED | 2024-12-30 | 45656.3729 | 2024-12-30 11:28 | 45656.4778 | 0.011181 | 7.4047e-05 | 1 | 151 | Unplanned | 6.0 Wildlife | Rat Blew 11kV Links @ Pole 22220
289 |  | F10631 | Taipo Rd | N/A | 414FED | 2024-12-30 | 45656.6 | 2024-12-30 14:40 | 45656.6111 | 0.0023695 | 0.00014809 | 2 | 32 | Unplanned | 8.0 Defective Equipment | Replacing Broken 11kV Dead End @ Pole 25081
290 |  | F4978 | 280 Parsons Rd | N/A | 430FED | 2025-01-04 | 45661.2799 | 2025-01-04 09:18 | 45661.3875 | 0.12277 | 0.0014809 | 20 | 1658 | Unplanned | 9.0 Cause Unknown | DDO Fused Tripped & Damaged @ Pole 16126
291 |  | F5016 | Oban St | N/A | 408FED | 2025-01-04 | 45661.4069 | 2025-01-04 10:15 | 45661.4271 | 0.13528 | 0.0046649 | 63 | 1827 | Unplanned | 8.0 Defective Equipment | CBS986 Tripped 11KV Cable Fault
292 |  | F16493 | Maungitiro | N/A | 413FED | 2025-01-08 | 45665.6514 | 2025-01-09 18:27 | 45666.7688 | 1.5028 | 0.0033321 | 45 | 20295 | Unplanned | 5.0 Third party Interference | Digger Hit 11kV Cable between Pole 10826 - Pole 18055
293 |  | F10647 | Otematata Station | N/A | 425FED | 2025-01-09 | 45666.2868 | 2025-01-09 08:27 | 45666.3521 | 0.0069604 | 7.4047e-05 | 1 | 94 | Unplanned | 6.0 Wildlife | Possom Blew 11kV Links Pole 71827
294 |  | NJ674 | Fuchsia Creek Rd | N/A | 483FED | 2025-01-13 | 45670.3354 | 2025-01-13 16:06 | 45670.6708 | 0.91744 | 0.0020733 | 28 | 12390 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms
295 |  | NJ675 | Fuchsia Creek Rd | N/A | 483FED | 2025-01-14 | 45671.3542 | 2025-01-14 16:03 | 45671.6687 | 1.0368 | 0.0023695 | 32 | 14002 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms
296 |  | F5021 | 250 Corbett Rd | N/A | 478FED | 2025-01-14 | 45671.6681 | 2025-01-14 18:48 | 45671.7833 | 0.037616 | 0.00074047 | 10 | 508 | Unplanned | 8.0 Defective Equipment | 11kV Jumper Burnt Off Line Side of DDO Pole 37033
297 |  | NJ676A | Fuchsia Creek Rd | N/A | 483FED | 2025-01-15 | 45672.3542 | 2025-01-15 15:58 | 45672.6653 | 0.92884 | 0.0020733 | 28 | 12544 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms, Installing 11kV Knife Links @ Pole 37710, Replacing Conductor between Pole 37711 & 17139
298 |  | NJ676B | Fuchsia Creek Rd | N/A | 483FED | 2025-01-16 | 45673.3542 | 2025-01-16 16:09 | 45673.6729 | 0.95165 | 0.0020733 | 28 | 12852 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms
299 |  | NJ677A | Fuchsia Creek Rd | N/A | 483FED | 2025-01-17 | 45674.3549 | 2025-01-17 14:42 | 45674.6125 | 0.40985 | 0.0011107 | 15 | 5535 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms, ABS1146 with 11kV Links, and Conductor between Pole 17139-30996
300 |  | NJ677B | Fuchsia Creek Rd | N/A | 483FED | 2025-01-20 | 45677.3549 | 2025-01-20 14:49 | 45677.6174 | 0.41762 | 0.0011107 | 15 | 5640 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms, ABS1146 with 11kV Links, and Conductor between Pole 17139-30996
301 |  | NJ677C | Fuchsia Creek Rd | N/A | 483FED | 2025-01-21 | 45678.3556 | 2025-01-21 13:34 | 45678.5653 | 0.33321 | 0.0011107 | 15 | 4500 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms, ABS1146 with 11kV Links, and Conductor between Pole 17139-30996
302 |  | PR312 | Redcastle Rd | N/A | 437FED | 2025-01-21 | 45678.3604 | 2025-01-21 15:34 | 45678.6486 | 0.030729 | 7.4047e-05 | 1 | 415 | Planned | 11.0 Planned Shutdown | Replacing 11kV Pot Head @ Pole 71888
303 |  | NJ598 | Roseberry Rd | N/A | 430FED | 2025-01-23 | 45680.3771 | 2025-01-23 12:35 | 45680.5243 | 0.094187 | 0.00044428 | 6 | 1272 | Planned | 11.0 Planned Shutdown | Replacing Pole 28169 & 28168
304 |  | PR313 | Corrigals Rd | N/A | 413FED | 2025-01-24 | 45681.3826 | 2025-01-24 15:44 | 45681.6556 | 0.1164 | 0.00029619 | 4 | 1572 | Planned | 11.0 Planned Shutdown | Replacing Pole 29346 and install Transformer
305 |  | F5430 | Uxbridge Rd | N/A | 444FED | 2025-01-27 | 45684.5604 | 2025-01-27 13:42 | 45684.5708 | 0.0088856 | 0.00059237 | 8 | 120 | Unplanned | 8.0 Defective Equipment | Re Fix Pole Cap @ Pole 23711
306 |  | F5246 | 26 Ridge Rd | N/A | 456FED | 2025-01-29 | 45686.3333 | 2025-01-29 08:59 | 45686.3743 | 0.017475 | 0.00029619 | 4 | 236 | Unplanned | 6.0 Wildlife | Rodent Blew 11kV Link Pole 42161
307 |  | PR322 | Whitestone Five Forks | N/A | 451FED | 2025-02-04 | 45692.3958 | 2025-02-04 12:57 | 45692.5396 | 0.33721 | 0.001629 | 22 | 4554 | Planned | 11.0 Planned Shutdown | Trimming Trees between Pole 27844 - Pole 39223
308 |  | NJ701 | Burnside Rd | N/A | 449FED | 2025-02-04 | 45692.3965 | 2025-02-04 11:58 | 45692.4986 | 0.15861 | 0.0011847 | 16 | 2142 | Planned | 11.0 Planned Shutdown | Shackle off 11KV Conductor @ Pole #27952 , Remove Conductor between Pole #27952 and Pole #71271 and Transformer @ Pole #71271
309 |  | NJ703 | Coal Pit Rd | N/A | 449FED | 2025-02-05 | 45693.3972 | 2025-02-05 13:05 | 45693.5451 | 0.23658 | 0.0011107 | 15 | 3195 | Planned | 11.0 Planned Shutdown | Replace Pole 24829 and install 11kV Links
310 |  | PR323 | Kauru Hill Rd | N/A | 415FED | 2025-02-05 | 45693.4187 | 2025-02-05 14:27 | 45693.6021 | 1.308 | 0.0049611 | 67 | 17664 | Planned | 11.0 Planned Shutdown | Trimming Trees between Pole 18552 - Pole 18566a/b
311 |  | F5034 | 90 Waiora Rd | N/A | 415FED | 2025-02-07 | 45695.2368 | 2025-02-07 06:21 | 45695.2646 | 0.0029619 | 7.4047e-05 | 1 | 40 | Unplanned | 6.0 Wildlife | Possom Blew 11kV Links @ Pole 12607
312 |  | PR325 | Otematata Station | N/A | 425FED | 2025-02-07 | 45695.3625 | 2025-02-07 13:48 | 45695.575 | 0.022658 | 7.4047e-05 | 1 | 306 | Planned | 11.0 Planned Shutdown | Felling Trees
313 |  | F4942 | 261 Peebles Siding Rd | N/A | 457FED | 2025-02-09 | 45697.4146 | 2025-02-09 12:20 | 45697.5139 | 0.34698 | 0.0048871 | 66 | 4686 | Unplanned | 8.0 Defective Equipment | 11kV Wire on Ground @ Pole 70837
314 |  | PR318 | Frew Rd | N/A | 417FED | 2025-02-10 | 45698.3486 | 2025-02-10 16:04 | 45698.6694 | 0.29478 | 0.0014069 | 19 | 3981 | Planned | 11.0 Planned Shutdown | Replacing Poles & Crossarms
315 |  | PR319A | Frew Rd and Herbert Rd | N/A | 417FED | 2025-02-11 | 45699.3521 | 2025-02-11 14:48 | 45699.6167 | 0.39496 | 0.0010367 | 14 | 5334 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and Conductor
316 |  | PR319B | Frew Rd and Herbert Rd | N/A | 417FED | 2025-02-12 | 45700.3486 | 2025-02-12 14:04 | 45700.5861 | 0.35454 | 0.0010367 | 14 | 4788 | Planned | 11.0 Planned Shutdown | Replace Poles, Crossarms and Conductor
317 |  | PR327 | Special School Rd | N/A | 494FED | 2025-02-14 | 45702.3632 | 2025-02-14 13:24 | 45702.5583 | 0.79067 | 0.0028138 | 38 | 10678 | Planned | 11.0 Planned Shutdown | Trimming Trees Between Pole 31949 and 31959
318 |  | NJ714 | Island Cliff Rd | N/A | 473FED | 2025-02-20 | 45708.3681 | 2025-02-20 12:49 | 45708.534 | 0.19467 | 0.00081451 | 11 | 2629 | Planned | 11.0 Planned Shutdown | Tightening 33kV and 11kV Lines
319 |  | NJ715 | Smillies Rd | N/A | 473FED | 2025-02-21 | 45709.3771 | 2025-02-21 11:47 | 45709.491 | 0.21859 | 0.0013328 | 18 | 2952 | Planned | 11.0 Planned Shutdown | Tightening Various 11kV Poles
320 |  | NJ722 | Shortland Rd | N/A | 304FED | 2025-02-24 | 45712.3549 | 2025-02-24 13:22 | 45712.5569 | 0.47405 | 0.001629 | 22 | 6402 | Planned | 11.0 Planned Shutdown | Tightening 33kV and 11kV Lines
321 |  | PI194A | Haka Valley Rd | N/A | 413FED | 2025-02-24 | 45712.3674 | 2025-02-24 15:44 | 45712.6556 | 0.58386 | 0.0014069 | 19 | 7885 | Planned | 11.0 Planned Shutdown | Replace Pole sand Crossarms
322 |  | NJ723 | TY Duncan Rd | N/A | 304FED | 2025-02-25 | 45713.3562 | 2025-02-25 11:05 | 45713.4618 | 0.033765 | 0.00022214 | 3 | 456 | Planned | 11.0 Planned Shutdown | Tightening 33kV and 11kV Lines
323 |  | PR333A | Haka Valley Rd | N/A | 413FED | 2025-02-25 | 45713.3667 | 2025-02-25 15:36 | 45713.65 | 0.57401 | 0.0014069 | 19 | 7752 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
324 |  | F5461 | Coal Pit Rd | N/A | 449FED | 2025-02-25 | 45713.3986 | 2025-02-25 11:27 | 45713.4771 | 0.025102 | 0.00022214 | 3 | 339 | Unplanned | 8.0 Defective Equipment | Change Transformer T2040
325 |  | F5044 | Peebles Area | N/A | 219FED | 2025-02-25 | 45713.5236 | 2025-02-25 15:23 | 45713.641 | 0.23599 | 0.0065902 | 89 | 3187 | Unplanned | 9.0 Cause Unknown | CB219 Peebles Tripped
326 |  | NJ725 | McCullock & Works Rd | N/A | 304FED | 2025-02-26 | 45714.3444 | 2025-02-26 13:32 | 45714.5639 | 0.14039 | 0.00044428 | 6 | 1896 | Planned | 11.0 Planned Shutdown | Tightening 33kV and 11kV Lines
327 |  | PR333B | Haka Valley Rd | N/A | 413FED | 2025-02-26 | 45714.3667 | 2025-02-26 13:30 | 45714.5625 | 0.39674 | 0.0014069 | 19 | 5358 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
328 |  | NJ732 | Mchenrys Rd | N/A | 413FED | 2025-02-27 | 45715.3556 | 2025-02-27 12:30 | 45715.5208 | 0.14098 | 0.00059237 | 8 | 1904 | Planned | 11.0 Planned Shutdown | Climbing and Tightening Patrol
329 |  | PR334 | Dansey Pass Rd | N/A | 421FED | 2025-02-28 | 45716.3646 | 2025-02-28 13:42 | 45716.5708 | 0.35187 | 0.0011847 | 16 | 4752 | Planned | 11.0 Planned Shutdown | Replace Pole 22836 and Maintenance
330 |  | NJ733 | Mchenrys Rd | N/A | 413FED | 2025-02-28 | 45716.3833 | 2025-02-28 15:15 | 45716.6354 | 0.34943 | 0.00096261 | 13 | 4719 | Planned | 11.0 Planned Shutdown | Climbing and Tightening Patrol
331 |  | F5466 | 82 Allan Rd | N/A | 483FED | 2025-03-03 | 45719.2833 | 2025-03-03 10:04 | 45719.4194 | 0.029026 | 0.00014809 | 2 | 392 | Unplanned | 6.0 Wildlife | Rat Blew DDO Fuse
332 |  | NJ734 | Mchenrys Rd | N/A | 413FED | 2025-03-03 | 45719.3611 | 2025-03-03 14:44 | 45719.6139 | 0.18867 | 0.00051833 | 7 | 2548 | Planned | 11.0 Planned Shutdown | Climbing and Tightening Patrol
333 |  | NJ748 | Reservoir Rd | N/A | 437FED | 2025-03-04 | 45720.3562 | 2025-03-04 10:12 | 45720.425 | 0.17593 | 0.0017771 | 24 | 2376 | Planned | 11.0 Planned Shutdown | Install 400A Disconnector and LV monitor
334 |  | PR336 | Special School Rd | N/A | 494FED | 2025-03-04 | 45720.3792 | 2025-03-04 13:32 | 45720.5639 | 0.72877 | 0.0027397 | 37 | 9842 | Planned | 11.0 Planned Shutdown | Installing 3 x DDOs and 30kVA Tx on Pole 31898
335 |  | NJ749 | Reservoir Rd | N/A | 437FED | 2025-03-04 | 45720.5208 | 2025-03-04 13:37 | 45720.5674 | 0.13395 | 0.0019993 | 27 | 1809 | Planned | 11.0 Planned Shutdown | Install 400A Disconnector and LV monitor
336 |  | F10745 | 49 Finlanys Rd | N/A | 420FED | 2025-03-05 | 45721.35 | 2025-03-05 09:44 | 45721.4056 | 0.0059237 | 7.4047e-05 | 1 | 80 | Unplanned | 6.0 Wildlife | Possom has caused DDOs to blow
337 |  | PR337 | Omarama-Otematata Rd | N/A | 423FED | 2025-03-05 | 45721.3507 | 2025-03-05 13:41 | 45721.5701 | 0.49137 | 0.001555 | 21 | 6636 | Planned | 11.0 Planned Shutdown | Remove 11kV Links on Pole 29693a/b. Replace pole 31079 and install top mount ABS
338 |  | F15997 | Yare St | N/A | 406FED | 2025-03-05 | 45721.9361 | 2025-03-05 23:00 | 45721.9583 | 2.9154 | 0.10218 | 1380 | 39372 | Unplanned | 6.0 Wildlife | Possum up Pole 16183 caused flashover
339 |  | F10749 | 129 Steward Rd | N/A | 432FED | 2025-03-06 | 45722.3542 | 2025-03-06 09:29 | 45722.3951 | 0.0087375 | 0.00014809 | 2 | 118 | Unplanned | 6.0 Wildlife | Blown DDO caused by rat
340 |  | NJ738 | Farm Rd | N/A | 413FED | 2025-03-07 | 45723.3542 | 2025-03-07 12:50 | 45723.5347 | 0.019252 | 7.4047e-05 | 1 | 260 | Planned | 11.0 Planned Shutdown | Replace Poles and Crossarms
341 |  | F5652 | 84 James Rd | N/A | 479FED | 2025-03-08 | 45724.3639 | 2025-03-08 09:15 | 45724.3854 | 0.0065161 | 7.4047e-05 | 1 | 88 | Unplanned | 6.0 Wildlife | Blown HV fuses
342 |  | NJ739 | Farm Rd | N/A | 413FED | 2025-03-10 | 45726.3556 | 2025-03-10 14:49 | 45726.6174 | 0.16749 | 0.00044428 | 6 | 2262 | Planned | 11.0 Planned Shutdown | Replace Poles 14406 and Tx
343 |  | NJ711 | Tokarahi Ngapara Rd | N/A | 308FED | 2025-03-10 | 45726.4222 | 2025-03-10 14:20 | 45726.5972 | 0.41051 | 0.001629 | 22 | 5544 | Planned | 11.0 Planned Shutdown | 33 & 11kV Tightening
344 |  | NJ740 | Milne Rd | N/A | 413FED | 2025-03-11 | 45727.3542 | 2025-03-11 14:52 | 45727.6194 | 0.31114 | 0.00081451 | 11 | 4202 | Planned | 11.0 Planned Shutdown | Replace Poles and Arms
345 |  | NJ745 | Lincoln St, Hampden | N/A | 480FED | 2025-03-11 | 45727.4285 | 2025-03-11 11:06 | 45727.4625 | 0.1415 | 0.0028878 | 39 | 1911 | Planned | 11.0 Planned Shutdown | Install LV Monitor
346 |  | NJ741 | Milne Rd | N/A | 413FED | 2025-03-12 | 45728.3556 | 2025-03-12 15:27 | 45728.6438 | 0.64532 | 0.001555 | 21 | 8715 | Planned | 11.0 Planned Shutdown | Replace Poles and Arms
347 |  | NJ756 | Lambton St | N/A | 416FED | 2025-03-13 | 45729.3792 | 2025-03-13 11:06 | 45729.4625 | 0.1866 | 0.001555 | 21 | 2520 | Planned | 11.0 Planned Shutdown | Install LV Monitor
348 |  | NJ757 | Beach Rd | N/A | 408FED | 2025-03-13 | 45729.5674 | 2025-03-13 15:50 | 45729.6597 | 0.21666 | 0.001629 | 22 | 2926 | Planned | 11.0 Planned Shutdown | Install LV Monitor
349 |  | NJ758 | Westview Drive | N/A | 427FED | 2025-03-14 | 45730.375 | 2025-03-14 10:37 | 45730.4424 | 0.19393 | 0.0019993 | 27 | 2619 | Planned | 11.0 Planned Shutdown | Install LV Monitor
350 |  | F5702 | 98 Springhill Rd | N/A | 428FED | 2025-03-14 | 45730.6569 | 2025-03-14 17:45 | 45730.7396 | 0.044058 | 0.00037023 | 5 | 595 | Unplanned | 5.0 Third party Interference | Digger hit 11kV Line near pole 25892
351 |  | PR342A | Tokarahi Tapui Rd | N/A | 421FED | 2025-03-18 | 45734.3431 | 2025-03-18 16:24 | 45734.6833 | 0.2177 | 0.00044428 | 6 | 2940 | Planned | 11.0 Planned Shutdown | Felling Trees between Pole 10076 and 10081
352 |  | F5658 | TY Duncan Rd | N/A | 432FED | 2025-03-18 | 45734.4007 | 2025-03-18 11:52 | 45734.4944 | 0.0099963 | 7.4047e-05 | 1 | 135 | Unplanned | 9.0 Cause Unknown | Blown DDOs - Cause Unknown
353 |  | NJ783 | Haka Highway | N/A | 412FED | 2025-03-18 | 45734.4903 | 2025-03-18 12:14 | 45734.5097 | 0.0020733 | 7.4047e-05 | 1 | 28 | Planned | 11.0 Planned Shutdown | Decomission Chorus Site
354 |  | PR342B | Tokarahi Tapui Rd | N/A | 421FED | 2025-03-19 | 45735.3333 | 2025-03-19 16:26 | 45735.6847 | 0.22481 | 0.00044428 | 6 | 3036 | Planned | 11.0 Planned Shutdown | Felling Trees
355 |  | NJ769 | Haka Valley Rd | N/A | 413FED | 2025-03-19 | 45735.3583 | 2025-03-19 16:00 | 45735.6667 | 0.52603 | 0.0011847 | 16 | 7104 | Planned | 11.0 Planned Shutdown | Replace Pole sand VLF cable
356 |  | NJ776 | Moorland Settlement Rd | N/A | 413FED | 2025-03-20 | 45736.3632 | 2025-03-20 12:57 | 45736.5396 | 0.075231 | 0.00029619 | 4 | 1016 | Planned | 11.0 Planned Shutdown | Replace Poles
357 |  | F12645 | Otiake Rd | N/A | 411FED | 2025-03-20 | 45736.4271 | 2025-03-20 11:17 | 45736.4701 | 0.1515 | 0.0024435 | 33 | 2046 | Unplanned | 5.0 Third party Interference | Report of Person trapped in tree near power lines
358 |  | PR344 | Shortland Rd | N/A | 432FED | 2025-03-21 | 45737.3528 | 2025-03-21 10:39 | 45737.4437 | 0.0097001 | 7.4047e-05 | 1 | 131 | Planned | 11.0 Planned Shutdown | Replace Tx with new 15kVA on pole 33203
359 |  | NJ777 | Menzies Rd | N/A | 413FED | 2025-03-21 | 45737.3576 | 2025-03-21 14:20 | 45737.5972 | 0.025546 | 7.4047e-05 | 1 | 345 | Planned | 11.0 Planned Shutdown | Replace Poles and tightening
360 |  | F5662 | 330 Springfield Rd | N/A | 416FED | 2025-03-24 | 45740.3507 | 2025-03-24 09:11 | 45740.3826 | 0.010218 | 0.00022214 | 3 | 138 | Unplanned | 6.0 Wildlife | Blown HV Fuses - Rats
361 |  | NJ778 | Haka Valley Rd | N/A | 413FED | 2025-03-25 | 45741.3819 | 2025-03-25 13:45 | 45741.5729 | 0.10181 | 0.00037023 | 5 | 1375 | Planned | 11.0 Planned Shutdown | Replace Pole 871620 and tightening
362 |  | NJ785 | Weston Rd | N/A | 427FED | 2025-03-25 | 45741.4174 | 2025-03-25 13:20 | 45741.5556 | 0.35365 | 0.0017771 | 24 | 4776 | Planned | 11.0 Planned Shutdown | Install LV Monitor
363 |  | NJ779 | Haka Valley Rd | N/A | 413FED | 2025-03-26 | 45742.3681 | 2025-03-26 15:13 | 45742.634 | 0.93588 | 0.0024435 | 33 | 12639 | Planned | 11.0 Planned Shutdown | Replace 11kV Pole 13186 and tightening
364 |  | NJ787 | Hilderthorpe Rd | N/A | 455FED | 2025-03-26 | 45742.5 | 2025-03-26 13:11 | 45742.5493 | 0.0052573 | 7.4047e-05 | 1 | 71 | Planned | 11.0 Planned Shutdown | Install LV Monitor
365 |  | NJ781 | Haka Valley Rd | N/A | 413FED | 2025-03-27 | 45743.4104 | 2025-03-27 15:33 | 45743.6479 | 0.32921 | 0.00096261 | 13 | 4446 | Planned | 11.0 Planned Shutdown | Replace Poles and Maintenance
366 |  | NJ750 | Main St, Weston | N/A | 428FED | 2025-03-28 | 45744.3625 | 2025-03-28 10:43 | 45744.4465 | 0.017919 | 0.00014809 | 2 | 242 | Planned | 11.0 Planned Shutdown | Install LV Monitor
367 |  | F12648 | Peebles Rd | N/A | 219FED | 2025-03-30 | 45746.3604 | 2025-03-30 09:35 | 45746.3993 | 0.087079 | 0.001555 | 21 | 1176 | Unplanned | 6.0 Wildlife | 11kV Conductor broken by Possum at Pole 2457
368 |  | NJ791 | Haka Valley Rd | N/A | 413FED | 2025-03-31 | 45747.3806 | 2025-03-31 13:48 | 45747.575 | 0.14513 | 0.00051833 | 7 | 1960 | Planned | 11.0 Planned Shutdown | Replace Crossarms and Maintenance
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
¹ Extend table as necessary to disclose information for all individual interruptions
Note on E286: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: On YE review - there was two duplicate NJ655 submissions not picked up when we submitted January 31 list. Corrected now